## Actuated Fail Close Checklist
|  |  | Commissioning Checklist |  | Project Top Gun
Garland, TX |  |  | Actuated Valves |  | CX-CL-XIS-FC
RED TAG
Valve Type |  | Two-Way Actuated Ball Valve |  | Power Medium | Compressed Air
Limit Switch |  | Mechanical |  | Fail Position | Closed
Safety: Verify that piping which valve is installed is in a safe state for valve operation (i.e. pipe not under pressure, piping does not contain liquid, no open ended pipe creating personnel exposure.)
Instructions: Perform the Activities as listed in the below checklist categories. Update the valve checklist to reflect checkout complete. Record any activity deficiencies on the checklist and ensure added to the punchlist for tracking. Some valves may have redundant solenoids and/or limit switches. Review the valve description and perform activities on any redundant devices to ensure completeness.
MECHANICAL
VALVE
| Activity ID |  | Activity Description
| XIS-FC-01 |  | Valve is installed in correct location per P&ID
| XIS-FC-02 |  | Valve name tag is present
| XIS-FC-03 |  | Flanges are gasketed and bolted
ACTUATOR
| Activity ID |  | Activity Description
| XIS-FC-04 |  | Verify actuator securely fastened to valve
| XIS-FC-05 |  | Installed such that position indicator can be seen (as much as possible)
| XIS-FC-06 |  | Solenoid air valve is tight to actuator
| XIS-FC-07 |  | Air filter installed into supply port of air valve; Muffler installed in exhaust port
| XIS-FC-08 |  | Compressed air tubing installed into filter
| XIS-FC-09 |  | Conduit attached to Top Hat and Solenoid
ELECTRICAL
SOLENOID
| Activity ID |  | Activity Description
| XIS-FC-10 |  | Output from PLC energizes appropriate solenoid to open actuated valve
| XIS-FC-11 |  | Actuated valve opens matching P&ID, valve location and Desktop HMI illustration
| XIS-FC-12 |  | Valve opens & closes minimum of 3 times without issue
| XIS-FC-13 |  | Valve opens & closes in Manual Mode
| XIS-FC-14 |  | While solenoid is energized, remove air and confirm valve fails to Closed position
LIMIT SWITCH
| Activity ID |  | Activity Description
| XIS-FC-15 |  | Input to PLC from switch feedback
| XIS-FC-16 |  | Switch feedback matches P&ID, valve location and Desktop HMI illustration
| XIS-FC-17 |  | Energized feedback (input=1) indicates valve is in Closed position
| XIS-FC-18 |  | De-Energized feedback (input=0) indicates valve is in the Open position
| XIS-FC-19 |  | Stall alarm triggers after 3 seconds with Activity XIS-FC-14
| XIS-FC-20 |  | Stall alarm triggers after 3 seconds with no air to solenoid when attempting to energize

## Actuated Fail Open Checklist
|  |  | Commissioning Checklist |  | Project Top Gun
Garland, TX |  |  | Actuated Valves |  | CX-CL-XIS-FO
RED TAG
Valve Type |  | Two-Way Actuated Ball Valve |  | Power Medium | Compressed Air
Limit Switch |  | Mechanical |  | Fail Position | OPEN
Safety: Verify that piping which valve is installed is in a safe state for valve operation (i.e. pipe not under pressure, piping does not contain liquid, no open ended pipe creating personnel exposure.)
Instructions: Perform the Activities as listed in the below checklist categories. Update the valve checklist to reflect checkout complete. Record any activity deficiencies on the checklist and ensure added to the punchlist for tracking. Some valves may have redundant solenoids and/or limit switches. Review the valve description and perform activities on any redundant devices to ensure completeness.
MECHANICAL
VALVE
| Activity ID |  | Activity Description
| XIS-FO-01 |  | Valve is installed in correct location per P&ID
| XIS-FO-02 |  | Valve name tag is present
| XIS-FO-03 |  | Flanges are gasketed and bolted
ACTUATOR
| Activity ID |  | Activity Description
| XIS-FO-04 |  | Verify actuator securely fastened to valve
| XIS-FO-05 |  | Installed such that position indicator can be seen (as much as possible)
| XIS-FO-06 |  | Solenoid air valve is tight to actuator
| XIS-FO-07 |  | Air filter installed into supply port of air valve; Muffler installed in exhaust port
| XIS-FO-08 |  | Compressed air tubing installed into filter
| XIS-FO-09 |  | Conduit attached to Top Hat and Solenoid
ELECTRICAL
SOLENOID
| Activity ID |  | Activity Description
| XIS-FO-10 |  | Output from PLC energizes appropriate solenoid to open actuated valve
| XIS-FO-11 |  | Actuated valve opens matching P&ID, valve location and Desktop HMI illustration
| XIS-FO-12 |  | Valve opens & closes minimum of 3 times without issue
| XIS-FO-13 |  | Valve opens & closes in Manual Mode
| XIS-FO-14 |  | While solenoid is energized, remove air and confirm valve fails to Open position
LIMIT SWITCH
| Activity ID |  | Activity Description
| XIS-FO-15 |  | Input to PLC from switch feedback
| XIS-FO-16 |  | Switch feedback matches P&ID, valve location and Desktop HMI illustration
| XIS-FO-17 |  | Energized feedback (input=1) indicates valve is in Open position
| XIS-FO-18 |  | De-Energized feedback (input=0) indicates valve is in the Close position
| XIS-FO-19 |  | Stall alarm triggers after 3 seconds with Activity XIS-FO-14
| XIS-FO-20 |  | Stall alarm triggers after 3 seconds with no air to solenoid when attempting to energize

## Actuated Fail Last Checklist
|  |  | Commissioning Checklist |  | Project Top Gun
Garland, TX |  |  | Actuated Valves |  | CX-CL-XIS-FL
RED TAG
Valve Type |  | Two-Way Actuated Ball Valve |  | Power Medium | Compressed Air
Limit Switch |  | Mechanical |  | Fail Position | LAST
Safety: Verify that piping which valve is installed is in a safe state for valve operation (i.e. pipe not under pressure, piping does not contain liquid, no open ended pipe creating personnel exposure.)
Instructions: Perform the Activities as listed in the below checklist categories. Update the valve checklist to reflect checkout complete. Record any activity deficiencies on the checklist and ensure added to the punchlist for tracking. Some valves may have redundant solenoids and/or limit switches. Review the valve description and perform activities on any redundant devices to ensure completeness.
MECHANICAL
VALVE
| Activity ID |  | Activity Description
| XIS-FL-01 |  | Valve is installed in correct location per P&ID
| XIS-FL-02 |  | Valve name tag is present
| XIS-FL-03 |  | Flanges are gasketed and bolted
ACTUATOR
| Activity ID |  | Activity Description
| XIS-FL-04 |  | Verify actuator securely fastened to valve
| XIS-FL-05 |  | Installed such that position indicator can be seen (as much as possible)
| XIS-FL-06 |  | Solenoid air valve is tight to actuator
| XIS-FL-07 |  | Air filter installed into supply port of air valve; Muffler installed in exhaust port
| XIS-FL-08 |  | Compressed air tubing installed into filter
| XIS-FL-09 |  | Conduit attached to Top Hat and Solenoid
ELECTRICAL
SOLENOID
| Activity ID |  | Activity Description
| XIS-FL-10 |  | Output from PLC energizes appropriate solenoid to open actuated valve
| XIS-FL-11 |  | Actuated valve opens matching P&ID, valve location and Desktop HMI illustration
| XIS-FL-12 |  | Valve opens & closes minimum of 3 times without issue
| XIS-FL-13 |  | Valve opens & closes in Manual Mode
| XIS-FL-14 |  | Solenoid 1 - While solenoid is energized, remove air and confirm valve fails in Last position
| XIS-FL-15 |  | Solenoid 2 - While solenoid is energized, remove air and confirm valve fails in Last position
LIMIT SWITCH
| Activity ID |  | Activity Description
| XIS-FL-16 |  | Input to PLC from switch feedback
| XIS-FL-17 |  | Switch feedback matches P&ID, valve location and Desktop HMI illustration
| XIS-FL-18 |  | Open Limit - Energized feedback (input=1) indicates valve is in Open position
| XIS-FL-19 |  | Open Limit - De-Energized feedback (input=0) indicates valve is not in Open position
| XIS-FL-20 |  | Closed Limit - Energized feedback (input=1) indicates valve is in Closed position
| XIS-FL-21 |  | Closed Limit - De-Energized feedback (input=0) indicates valve is in not in Closed position
| XIS-FL-22 |  | Remove air and attempt to change position. Confirm Stall Timer triggers in 3 seconds
| XIS-FL-23 |  | Stall alarm triggers after 3 seconds with no air to solenoids when attempting to energize

## Control Fail Open Checklist
|  |  | Commissioning Checklist |  | Project Top Gun
Garland, TX |  |  | Flow / Temperature Control Valve |  | CX-CL-FIC-FO
RED TAG
Valve Type |  | Proportional Control Valve |  | Power Medium | Compressed Air
Limit Switch |  | Mechanical |  | Fail Position | OPEN
Safety: Verify that piping which valve is installed is in a safe state for valve operation (i.e. pipe not under pressure, piping does not contain liquid, no open ended pipe creating personnel exposure.)
Instructions: Perform the Activities as listed in the below checklist categories. Update the valve checklist to reflect checkout complete. Record any activity deficiencies on the checklist and ensure added to the punchlist for tracking. These valves are similar but different to the other actuated valves. Be sure to check the multiple positions as outlined in the activity list
MECHANICAL
VALVE
| Activity ID |  | Activity Description
| FIC-FO-01 |  | Valve is installed in correct location per P&ID
| FIC-FO-02 |  | Valve name tag is present
| FIC-FO-03 |  | Flanges are gasketed and bolted
ACTUATOR
| Activity ID |  | Activity Description
| FIC-FO-04 |  | Verify actuator securely fastened to valve
| FIC-FO-05 |  | Installed such that position indicator can be seen (as much as possible)
| FIC-FO-06 |  | Solenoid air valve is tight to actuator
| FIC-FO-07 |  | Air filter installed into supply port of air valve; Muffler installed in exhaust port
| FIC-FO-08 |  | Compressed air tubing installed into filter
| FIC-FO-09 |  | Conduit attached to Top Hat and Solenoid
ELECTRICAL
VALVE CONTROLLER
| Activity ID |  | Activity Description
| FIC-FO-10 |  | Output from PLC energizes appropriate solenoid to open actuated valve
| FIC-FO-11 |  | Control valve opens matching P&ID, valve location and Desktop HMI illustration
| FIC-FO-12 |  | From Closed (0%) open valve to 25%, 50%, 75%, 100% and validate position
| FIC-FO-13 |  | From Open (100%) close valve to 75%, 50%, 25%,0% and validate position
| FIC-FO-14 |  | While controller is energized, remove air and confirm valve fails to Open position

## Control Fail Close Checklist
|  |  | Commissioning Checklist |  | Project Top Gun
Garland, TX |  |  | Flow / Temperature Control Valve |  | CX-CL-FIC-FC
RED TAG
Valve Type |  | Proportional Control Valve |  | Power Medium | Compressed Air
Limit Switch |  | Mechanical |  | Fail Position | CLOSED
Safety: Verify that piping which valve is installed is in a safe state for valve operation (i.e. pipe not under pressure, piping does not contain liquid, no open ended pipe creating personnel exposure.)
Instructions: Perform the Activities as listed in the below checklist categories. Update the valve checklist to reflect checkout complete. Record any activity deficiencies on the checklist and ensure added to the punchlist for tracking. These valves are similar but different to the other actuated valves. Be sure to check the multiple positions as outlined in the activity list
MECHANICAL
VALVE
| Activity ID |  | Activity Description
| FIC-FC-01 |  | Valve is installed in correct location per P&ID
| FIC-FC-02 |  | Valve name tag is present
| FIC-FC-03 |  | Flanges are gasketed and bolted
ACTUATOR
| Activity ID |  | Activity Description
| FIC-FC-04 |  | Verify actuator securely fastened to valve
| FIC-FC-05 |  | Installed such that position indicator can be seen (as much as possible)
| FIC-FC-06 |  | Solenoid air valve is tight to actuator
| FIC-FC-07 |  | Air filter installed into supply port of air valve; Muffler installed in exhaust port
| FIC-FC-08 |  | Compressed air tubing installed into filter
| FIC-FC-09 |  | Conduit attached to Top Hat and Solenoid
ELECTRICAL
VALVE CONTROLLER
| Activity ID |  | Activity Description
| FIC-FC-10 |  | Output from PLC energizes appropriate solenoid to open actuated valve
| FIC-FC-11 |  | Control valve opens matching P&ID, valve location and Desktop HMI illustration
| FIC-FC-12 |  | From Closed (0%) open valve to 25%, 50%, 75%, 100% to validate position
| FIC-FC-13 |  | From Open (100%) close valve to 75%, 50%, 25%,0% to validate position
| FIC-FC-14 |  | While controller is energized, remove air and confirm valve fails to Closed position

## New Actuated Valve List
Valve Number | P&ID | System | Location | Descriptive Name | Valve Type | Solenoid Output Address | Closed Limit Switch Input | Open Limit Switch Input | Checklist | Team Member | Date | Pass (Y) or (N) | Comment
XIS_96301 |  | MFG1 |  | Vanne Alimentation Process en Eua Froide |  | JB_Z1_101:1:O.Pt01.Data | JB_Z1_101:3:I.Pt02.Data | JB_Z1_101:3:I.Pt01.Data
XIS_96208 |  | MFG1 |  | Vanne Alimentation HVAC en Eua Froide |  | JB_Z1_101:1:O.Pt02.Data | JB_Z1_101:3:I.Pt04.Data | JB_Z1_101:3:I.Pt03.Data
XIS_43020 |  | MFG1 |  | Vanne Alimentation V43000 Venant du V410 |  | JB_Z3_131:1:O.Pt01.Data | JB_Z3_131:4:I.Pt02.Data | JB_Z3_131:4:I.Pt01.Data
XIS_43017 |  | MFG1 |  | Vanne Alimentation V44000 Venant du V400 |  | JB_Z3_131:1:O.Pt02.Data | JB_Z3_131:4:I.Pt04.Data | JB_Z3_131:4:I.Pt03.Data
XIS_43016 |  | MFG1 |  | Vanne Alimentation V44000 Venant du V410 |  | JB_Z3_131:2:O.Pt01.Data | JB_Z3_131:4:I.Pt06.Data | JB_Z3_131:4:I.Pt05.Data
XIS_43013 |  | MFG1 |  | Vanne Alimentation V43000 Venant du V400 |  | JB_Z3_131:2:O.Pt02.Data | JB_Z3_131:4:I.Pt08.Data | JB_Z3_131:4:I.Pt07.Data
XIS_40707 |  | MFG1 |  | Vanne Azote de purge après Filtre F40700 |  | JB_Z4_101_01:1:O.Pt01.Data | JB_Z4_101_01:13:I.Pt02.Data | JB_Z4_101_01:13:I.Pt01.Data
XIS_40706 |  | MFG1 |  | Vanne Azote de purge filtres F40700 |  | JB_Z4_101_01:1:O.Pt02.Data | JB_Z4_101_01:13:I.Pt04.Data | JB_Z4_101_01:13:I.Pt03.Data
XIS_40705 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_101_01:2:O.Pt01.Data | JB_Z4_101_01:13:I.Pt06.Data | JB_Z4_101_01:13:I.Pt05.Data
XIS_40703 |  | MFG1 |  | Vanne arrivée produit ver F40700 |  | JB_Z4_101_01:2:O.Pt02.Data | JB_Z4_101_01:13:I.Pt08.Data | JB_Z4_101_01:13:I.Pt07.Data
XIS_40702 |  | MFG1 |  | Vanne de Séparation F40600 et F40700 |  | JB_Z4_101_01:3:O.Pt01.Data | JB_Z4_101_01:14:I.Pt02.Data | JB_Z4_101_01:14:I.Pt01.Data
XIS_40605 |  | MFG1 |  | Vanne Azote de purge Filtre F40600 |  | JB_Z4_101_01:3:O.Pt02.Data | JB_Z4_101_01:14:I.Pt04.Data | JB_Z4_101_01:14:I.Pt03.Data
XIS_40604 |  | MFG1 |  | Vanne séparation F40400/F40500 et F40600 |  | JB_Z4_101_01:4:O.Pt01.Data | JB_Z4_101_01:14:I.Pt06.Data | JB_Z4_101_01:14:I.Pt05.Data
XIS_40602 |  | MFG1 |  | Vanne arrivée produit ver F40600 |  | JB_Z4_101_01:4:O.Pt02.Data | JB_Z4_101_01:14:I.Pt08.Data | JB_Z4_101_01:14:I.Pt07.Data
XIS_40507 |  | MFG1 |  | Vanne Azote de purge après Filtre F40500 |  | JB_Z4_101_01:5:O.Pt01.Data | JB_Z4_101_01:15:I.Pt02.Data | JB_Z4_101_01:15:I.Pt01.Data
XIS_40506 |  | MFG1 |  | Vanne Azote de purge Filtre F40500 |  | JB_Z4_101_01:5:O.Pt02.Data | JB_Z4_101_01:15:I.Pt04.Data | JB_Z4_101_01:15:I.Pt03.Data
XIS_40505 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_101_01:6:O.Pt01.Data | JB_Z4_101_01:15:I.Pt06.Data | JB_Z4_101_01:15:I.Pt05.Data
XIS_40503 |  | MFG1 |  | Vanne arrivée produit ver F40500 |  | JB_Z4_101_01:6:O.Pt02.Data | JB_Z4_101_01:15:I.Pt08.Data | JB_Z4_101_01:15:I.Pt07.Data
XIS_40502 |  | MFG1 |  | Vanne de Séparation F40400 et F40500 |  | JB_Z4_101_01:7:O.Pt01.Data | JB_Z4_101_01:16:I.Pt02.Data | JB_Z4_101_01:16:I.Pt01.Data
XIS_40405 |  | MFG1 |  | Vanne Azote de purge Filtre F40400 |  | JB_Z4_101_01:7:O.Pt02.Data | JB_Z4_101_01:16:I.Pt04.Data | JB_Z4_101_01:16:I.Pt03.Data
XIS_40404 |  | MFG1 |  | Vanne séparation F40600/F40700 et F40400 |  | JB_Z4_101_01:8:O.Pt01.Data | JB_Z4_101_01:16:I.Pt06.Data | JB_Z4_101_01:16:I.Pt05.Data
XIS_40402 |  | MFG1 |  | Vanne arrivée produit ver F40400 |  | JB_Z4_101_01:8:O.Pt02.Data | JB_Z4_101_01:16:I.Pt08.Data | JB_Z4_101_01:16:I.Pt07.Data
XIS_40312 |  | MFG1 |  | Vanne de Recirculation V40000 après filt |  | JB_Z4_101_01:9:O.Pt01.Data | JB_Z4_101_01:17:I.Pt02.Data | JB_Z4_101_01:17:I.Pt01.Data
XIS_40309 |  | MFG1 |  | Vanne d$'envoie de V40000 vers Cuves de |  | JB_Z4_101_01:9:O.Pt02.Data | JB_Z4_101_01:17:I.Pt04.Data | JB_Z4_101_01:17:I.Pt03.Data
XIS_40306 |  | MFG1 |  | Vanne de Recirculation V40000 avant filt |  | JB_Z4_101_01:10:O.Pt01.Data | JB_Z4_101_01:17:I.Pt06.Data | JB_Z4_101_01:17:I.Pt05.Data
XIS_40301 |  | MFG1 |  | Vanne de Fond de cuve de Filtration V400 |  | JB_Z4_101_01:10:O.Pt02.Data | JB_Z4_101_01:17:I.Pt08.Data | JB_Z4_101_01:17:I.Pt07.Data
SPARE_XIS |  | MFG1 |  |  |  | None | None | None
SPARE_XIS |  | MFG1 |  |  |  | None | None | None
XIS_40046 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_101_01:12:O.Pt01.Data | JB_Z4_101_01:18:I.Pt06.Data | JB_Z4_101_01:18:I.Pt05.Data
XIS_40045 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_101_01:12:O.Pt02.Data | JB_Z4_101_01:18:I.Pt08.Data | JB_Z4_101_01:18:I.Pt07.Data
XIS_40044 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_101_02:1:O.Pt01.Data | JB_Z4_101_02:5:I.Pt02.Data | JB_Z4_101_02:5:I.Pt01.Data
XIS_40043 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_101_02:1:O.Pt02.Data | JB_Z4_101_02:5:I.Pt04.Data | JB_Z4_101_02:5:I.Pt03.Data
XIS_40042 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_101_02:2:O.Pt01.Data | JB_Z4_101_02:5:I.Pt06.Data | JB_Z4_101_02:5:I.Pt05.Data
XIS_40026 |  | MFG1 |  | Vanne d$'arriée Azote Pour Flush ligne p |  | JB_Z4_101_02:2:O.Pt02.Data | JB_Z4_101_02:5:I.Pt08.Data | JB_Z4_101_02:5:I.Pt07.Data
XIS_40025 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée double envel |  | JB_Z4_101_02:3:O.Pt01.Data | JB_Z4_101_02:6:I.Pt02.Data | JB_Z4_101_02:6:I.Pt01.Data
XIS_40024 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_101_02:3:O.Pt02.Data | JB_Z4_101_02:6:I.Pt04.Data | JB_Z4_101_02:6:I.Pt03.Data
XIS_41707 |  | MFG1 |  | Vanne Azote de purge après Filtre F41700 |  | JB_Z4_102_01:1:O.Pt01.Data | JB_Z4_102_01:13:I.Pt02.Data | JB_Z4_102_01:13:I.Pt01.Data
XIS_41706 |  | MFG1 |  | Vanne Azote de purge filtres F41700 |  | JB_Z4_102_01:1:O.Pt02.Data | JB_Z4_102_01:13:I.Pt04.Data | JB_Z4_102_01:13:I.Pt03.Data
XIS_41705 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_102_01:2:O.Pt01.Data | JB_Z4_102_01:13:I.Pt06.Data | JB_Z4_102_01:13:I.Pt05.Data
XIS_41703 |  | MFG1 |  | Vanne arrivée produit ver F41700 |  | JB_Z4_102_01:2:O.Pt02.Data | JB_Z4_102_01:13:I.Pt08.Data | JB_Z4_102_01:13:I.Pt07.Data
XIS_41702 |  | MFG1 |  | Vanne de Séparation F41600 et F41700 |  | JB_Z4_102_01:3:O.Pt01.Data | JB_Z4_102_01:14:I.Pt02.Data | JB_Z4_102_01:14:I.Pt01.Data
XIS_41605 |  | MFG1 |  | Vanne Azote de purge Filtre F41600 |  | JB_Z4_102_01:3:O.Pt02.Data | JB_Z4_102_01:14:I.Pt04.Data | JB_Z4_102_01:14:I.Pt03.Data
XIS_41604 |  | MFG1 |  | Vanne séparation F41400/F41500 et F41600 |  | JB_Z4_102_01:4:O.Pt01.Data | JB_Z4_102_01:14:I.Pt06.Data | JB_Z4_102_01:14:I.Pt05.Data
XIS_41602 |  | MFG1 |  | Vanne arrivée produit ver F41600 |  | JB_Z4_102_01:4:O.Pt02.Data | JB_Z4_102_01:14:I.Pt08.Data | JB_Z4_102_01:14:I.Pt07.Data
XIS_41507 |  | MFG1 |  | Vanne Azote de purge après Filtre F41500 |  | JB_Z4_102_01:5:O.Pt01.Data | JB_Z4_102_01:15:I.Pt02.Data | JB_Z4_102_01:15:I.Pt01.Data
XIS_41506 |  | MFG1 |  | Vanne Azote de purge Filtre F41500 |  | JB_Z4_102_01:5:O.Pt02.Data | JB_Z4_102_01:15:I.Pt04.Data | JB_Z4_102_01:15:I.Pt03.Data
XIS_41505 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_102_01:6:O.Pt01.Data | JB_Z4_102_01:15:I.Pt06.Data | JB_Z4_102_01:15:I.Pt05.Data
XIS_41503 |  | MFG1 |  | Vanne arrivée produit ver F41500 |  | JB_Z4_102_01:6:O.Pt02.Data | JB_Z4_102_01:15:I.Pt08.Data | JB_Z4_102_01:15:I.Pt07.Data
XIS_41502 |  | MFG1 |  | Vanne de Séparation F41400 et F41500 |  | JB_Z4_102_01:7:O.Pt01.Data | JB_Z4_102_01:16:I.Pt02.Data | JB_Z4_102_01:16:I.Pt01.Data
XIS_41405 |  | MFG1 |  | Vanne Azote de purge Filtre F41400 |  | JB_Z4_102_01:7:O.Pt02.Data | JB_Z4_102_01:16:I.Pt04.Data | JB_Z4_102_01:16:I.Pt03.Data
XIS_41404 |  | MFG1 |  | Vanne séparation F41600/F41700 et F41400 |  | JB_Z4_102_01:8:O.Pt01.Data | JB_Z4_102_01:16:I.Pt06.Data | JB_Z4_102_01:16:I.Pt05.Data
XIS_41402 |  | MFG1 |  | Vanne arrivée produit ver F41400 |  | JB_Z4_102_01:8:O.Pt02.Data | JB_Z4_102_01:16:I.Pt08.Data | JB_Z4_102_01:16:I.Pt07.Data
XIS_41312 |  | MFG1 |  | Vanne de Recirculation V41000 après filt |  | JB_Z4_102_01:9:O.Pt01.Data | JB_Z4_102_01:17:I.Pt02.Data | JB_Z4_102_01:17:I.Pt01.Data
XIS_41307 |  | MFG1 |  | Vanne d$'envoie de V41000 vers Cuves de |  | JB_Z4_102_01:9:O.Pt02.Data | JB_Z4_102_01:17:I.Pt04.Data | JB_Z4_102_01:17:I.Pt03.Data
XIS_41306 |  | MFG1 |  | Vanne de Recirculation V41000 avant filt |  | JB_Z4_102_01:10:O.Pt01.Data | JB_Z4_102_01:17:I.Pt06.Data | JB_Z4_102_01:17:I.Pt05.Data
XIS_41301 |  | MFG1 |  | Vanne de Fond de cuve de Filtration V410 |  | JB_Z4_102_01:10:O.Pt02.Data | JB_Z4_102_01:17:I.Pt08.Data | JB_Z4_102_01:17:I.Pt07.Data
XIS_41046 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_102_01:11:O.Pt01.Data | JB_Z4_102_01:18:I.Pt02.Data | JB_Z4_102_01:18:I.Pt01.Data
XIS_41045 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_102_01:11:O.Pt02.Data | JB_Z4_102_01:18:I.Pt04.Data | JB_Z4_102_01:18:I.Pt03.Data
XIS_41043 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_102_02:1:O.Pt01.Data | JB_Z4_102_02:5:I.Pt02.Data | JB_Z4_102_02:5:I.Pt01.Data
XIS_41042 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_102_02:1:O.Pt02.Data | JB_Z4_102_02:5:I.Pt04.Data | JB_Z4_102_02:5:I.Pt03.Data
XIS_41013 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée double envel |  | JB_Z4_102_02:2:O.Pt01.Data | JB_Z4_102_02:5:I.Pt06.Data | JB_Z4_102_02:5:I.Pt05.Data
XIS_41012 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_102_02:2:O.Pt02.Data | JB_Z4_102_02:5:I.Pt08.Data | JB_Z4_102_02:5:I.Pt07.Data
XIS_41010 |  | MFG1 |  | Vanne d$'arriée Azote Pour Flush ligne p |  | JB_Z4_102_02:3:O.Pt01.Data | JB_Z4_102_02:6:I.Pt02.Data | JB_Z4_102_02:6:I.Pt01.Data
XIS_42409 |  | MFG1 |  | Vanne de Recirculation V42000 après filt |  | JB_Z4_103:1:O.Pt01.Data | JB_Z4_103:12:I.Pt02.Data | JB_Z4_103:12:I.Pt01.Data
XIS_42408 |  | MFG1 |  | Vanne d$'envoie de V42000 vers Cuves de |  | JB_Z4_103:1:O.Pt02.Data | JB_Z4_103:12:I.Pt04.Data | JB_Z4_103:12:I.Pt03.Data
XIS_42406 |  | MFG1 |  | Vanne de Recirculation V42000 avant filt |  | JB_Z4_103:2:O.Pt01.Data | JB_Z4_103:12:I.Pt06.Data | JB_Z4_103:12:I.Pt05.Data
XIS_42301 |  | MFG1 |  | Vanne de Fond de cuve de Filtration V420 |  | JB_Z4_103:2:O.Pt02.Data | JB_Z4_103:12:I.Pt08.Data | JB_Z4_103:12:I.Pt07.Data
XIS_42047 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_103:4:O.Pt01.Data | JB_Z4_103:13:I.Pt02.Data | JB_Z4_103:13:I.Pt01.Data
XIS_42046 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_103:4:O.Pt02.Data | JB_Z4_103:13:I.Pt04.Data | JB_Z4_103:13:I.Pt03.Data
XIS_42045 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_103:5:O.Pt01.Data | JB_Z4_103:13:I.Pt06.Data | JB_Z4_103:13:I.Pt05.Data
XIS_42044 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_103:5:O.Pt02.Data | JB_Z4_103:13:I.Pt08.Data | JB_Z4_103:13:I.Pt07.Data
XIS_42043 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_103:6:O.Pt01.Data | JB_Z4_103:14:I.Pt02.Data | JB_Z4_103:14:I.Pt01.Data
XIS_42042 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z4_103:6:O.Pt02.Data | JB_Z4_103:14:I.Pt04.Data | JB_Z4_103:14:I.Pt03.Data
XIS_42020 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée double envel |  | JB_Z4_103:7:O.Pt01.Data | JB_Z4_103:14:I.Pt06.Data | JB_Z4_103:14:I.Pt05.Data
XIS_42402 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_103:7:O.Pt02.Data | JB_Z4_103:15:I.Pt04.Data | JB_Z4_103:15:I.Pt03.Data
XIS_42006 |  | MFG1 |  | Vanne d$'arriée Azote Pour Flush ligne p |  | JB_Z4_103:8:O.Pt01.Data | JB_Z4_103:14:I.Pt08.Data | JB_Z4_103:14:I.Pt07.Data
XIS_42401 |  | MFG1 |  | Vanne d$'arrivée produit F42400 |  | JB_Z4_103:8:O.Pt02.Data | JB_Z4_103:15:I.Pt02.Data | JB_Z4_103:15:I.Pt01.Data
XIS_42501 |  | MFG1 |  | Vanne d$'arrivée produit F42500 |  | JB_Z4_103:9:O.Pt01.Data | JB_Z4_103:15:I.Pt06.Data | JB_Z4_103:15:I.Pt05.Data
XIS_42502 |  | MFG1 |  | Vanne d$'envoie vers Cuves de Stockges a |  | JB_Z4_103:9:O.Pt02.Data | JB_Z4_103:15:I.Pt08.Data | JB_Z4_103:15:I.Pt07.Data
XIS_42503 |  | MFG1 |  | Vanne Azote de purge Filtre F42400 |  | JB_Z4_103:10:O.Pt01.Data | JB_Z4_103:16:I.Pt02.Data | JB_Z4_103:16:I.Pt01.Data
XIS_42403 |  | MFG1 |  | Vanne Azote de purge Filtre F42500 |  | JB_Z4_103:10:O.Pt02.Data | JB_Z4_103:16:I.Pt04.Data | JB_Z4_103:16:I.Pt03.Data
XIS_42017 |  | MFG1 |  | Vanne Azote pour Inhertage V42000 |  | JB_Z4_121_01:1:O.Pt01.Data | JB_Z4_121_01:6:I.Pt02.Data | JB_Z4_121_01:6:I.Pt01.Data
XIS_42011 |  | MFG1 |  | Vanne d$'arrivé produit de R35000 vers V |  | JB_Z4_121_01:1:O.Pt02.Data | JB_Z4_121_01:6:I.Pt04.Data | JB_Z4_121_01:6:I.Pt03.Data
XIS_41007 |  | MFG1 |  | Vanne Azote pour Inhertage V41000 |  | JB_Z4_121_01:2:O.Pt01.Data | JB_Z4_121_01:6:I.Pt06.Data | JB_Z4_121_01:6:I.Pt05.Data
XIS_41002 |  | MFG1 |  | Vanne d$'arrivé produit de R34000 vers V |  | JB_Z4_121_01:2:O.Pt02.Data | JB_Z4_121_01:6:I.Pt08.Data | JB_Z4_121_01:6:I.Pt07.Data
XIS_40014 |  | MFG1 |  | Vanne d$'arrivé produit de R33000 vers V |  | JB_Z4_121_01:3:O.Pt01.Data | JB_Z4_121_01:7:I.Pt02.Data | JB_Z4_121_01:7:I.Pt01.Data
XIS_40028 |  | MFG1 |  | Vanne Azote pour Inhertage V40000 |  | JB_Z4_121_01:3:O.Pt02.Data | JB_Z4_121_01:7:I.Pt04.Data | JB_Z4_121_01:7:I.Pt03.Data
XIS_40013 |  | MFG1 |  | Vanne Alimentaion produit R34000 vers V4 |  | JB_Z4_121_01:4:O.Pt01.Data | JB_Z4_121_01:7:I.Pt06.Data | JB_Z4_121_01:7:I.Pt05.Data
XIS_41003 |  | MFG1 |  | Vanne Alimentaion produit Venant du ER33 |  | JB_Z4_121_01:4:O.Pt02.Data | JB_Z4_121_01:7:I.Pt08.Data | JB_Z4_121_01:7:I.Pt07.Data
XIS_41044 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe |  | JB_Z4_121_01:5:O.Pt01.Data | JB_Z4_121_01:8:I.Pt02.Data | JB_Z4_121_01:8:I.Pt01.Data
XIS_88019 |  | MFG1 |  | Vanne de Recirculation T88000 |  | JB_Z5_101:1:O.Pt01.Data | JB_Z5_101:3:I.Pt02.Data | JB_Z5_101:3:I.Pt01.Data
XIS_87018 |  | MFG1 |  | Vanne de Recirculation T87000 |  | JB_Z5_101:1:O.Pt02.Data | JB_Z5_101:3:I.Pt04.Data | JB_Z5_101:3:I.Pt03.Data
XIS_86019 |  | MFG1 |  | Vanne de Recirculation T86000 |  | JB_Z5_101:2:O.Pt02.Data | JB_Z5_101:3:I.Pt06.Data | JB_Z5_101:3:I.Pt05.Data
XIS_33042 |  | MFG1 |  | Vanne Azote Grand Débit pour Flush Ligne |  | JB_Z6_101:1:O.Pt01.Data | JB_Z6_101:10:I.Pt02.Data | JB_Z6_101:10:I.Pt01.Data
XIS_33701 |  | MFG1 |  | Vanne de Fond de Cuve R33000 |  | JB_Z6_101:1:O.Pt02.Data | JB_Z6_101:10:I.Pt04.Data | JB_Z6_101:10:I.Pt03.Data
XIS_33031 |  | MFG1 |  | Vanne d$'Arrivée Vapeur Double Enveloppe |  | JB_Z6_101:2:O.Pt01.Data | JB_Z6_101:10:I.Pt06.Data | JB_Z6_101:10:I.Pt05.Data
XIS_33025 |  | MFG1 |  | Vanne de fond de cuve R33000 |  | JB_Z6_101:2:O.Pt02.Data | JB_Z6_101:10:I.Pt08.Data | JB_Z6_101:10:I.Pt07.Data
XIS_34701 |  | MFG1 |  | Vanne de fond de cuve R34000 |  | JB_Z6_101:3:O.Pt01.Data | JB_Z6_101:11:I.Pt02.Data | JB_Z6_101:11:I.Pt01.Data
XIS_34051 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe |  | JB_Z6_101:3:O.Pt02.Data | JB_Z6_101:11:I.Pt04.Data | JB_Z6_101:11:I.Pt03.Data
XIS_34042 |  | MFG1 |  | Vanne Azote Grand Débit pour Flush Ligne |  | JB_Z6_101:4:O.Pt01.Data | JB_Z6_101:11:I.Pt06.Data | JB_Z6_101:11:I.Pt05.Data
XIS_34040 |  | MFG1 |  | Vanne Arrivée Pour Flush Ligne Rpoduit R34000 |  | JB_Z6_101:4:O.Pt02.Data | JB_Z6_101:11:I.Pt08.Data | JB_Z6_101:11:I.Pt07.Data
XIS_34018 |  | MFG1 |  | Vanne D$'arrivée Azote Pour Bullage R34000 |  | JB_Z6_101:5:O.Pt01.Data | JB_Z6_101:12:I.Pt02.Data | JB_Z6_101:12:I.Pt01.Data
XIS_33051 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe R34000 partie milieu |  | JB_Z6_101:5:O.Pt02.Data | JB_Z6_101:12:I.Pt04.Data | JB_Z6_101:12:I.Pt03.Data
XIS_33050 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe R34000 partie haute |  | JB_Z6_101:6:O.Pt01.Data | JB_Z6_101:12:I.Pt06.Data | JB_Z6_101:12:I.Pt05.Data
XIS_40220 |  | MFG1 |  | Vanne d$'arrivée produit IBC Vers V40000 |  | JB_Z6_101:6:O.Pt02.Data | JB_Z6_101:12:I.Pt08.Data | JB_Z6_101:12:I.Pt07.Data
XIS_40207 |  | MFG1 |  | Vanne d$'arrivé air sur Pompe P40200 |  | JB_Z6_101:7:O.Pt01.Data | JB_Z6_101:13:I.Pt02.Data | JB_Z6_101:13:I.Pt01.Data
XIS_41220 |  | MFG1 |  | Vanne d$'arrivée produit IBC Vers V41000 |  | JB_Z6_101:7:O.Pt02.Data | JB_Z6_101:13:I.Pt04.Data | JB_Z6_101:13:I.Pt03.Data
XIS_41204 |  | MFG1 |  | Vanne d$'arricé air sur Pompe P41200 |  | JB_Z6_101:8:O.Pt01.Data | JB_Z6_101:13:I.Pt06.Data | JB_Z6_101:13:I.Pt05.Data
XIS_42220 |  | MFG1 |  | Vanne d$'Arrivée Produit venant du IBC vers V42000 |  | JB_Z6_101:8:O.Pt02.Data | JB_Z6_101:13:I.Pt08.Data | JB_Z6_101:13:I.Pt07.Data
XIS_42204 |  | MFG1 |  | Vanne d$'arrivé air sur Pompe P42200 |  | JB_Z6_101:9:O.Pt01.Data | JB_Z6_101:14:I.Pt02.Data | JB_Z6_101:14:I.Pt01.Data
XIS_34004 |  | MFG1 |  |  |  | JB_Z6_101:9:O.Pt02.Data | JB_Z6_101:14:I.Pt04.Data | JB_Z6_101:14:I.Pt03.Data
XIS_35701 |  | MFG1 |  | Vanne de Fond de Cuver R35000 |  | JB_Z6_102:1:O.Pt01.Data | JB_Z6_102:11:I.Pt02.Data | JB_Z6_102:11:I.Pt01.Data
XIS_35052 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R35000 partie milieu |  | JB_Z6_102:1:O.Pt02.Data | JB_Z6_102:11:I.Pt04.Data | JB_Z6_102:11:I.Pt03.Data
XIS_35051 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe R35000 partie milieu |  | JB_Z6_102:2:O.Pt01.Data | JB_Z6_102:11:I.Pt06.Data | JB_Z6_102:11:I.Pt05.Data
XIS_35050 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe R35000 partie haute |  | JB_Z6_102:2:O.Pt02.Data | JB_Z6_102:11:I.Pt08.Data | JB_Z6_102:11:I.Pt07.Data
XIS_35045 |  | MFG1 |  | Vanne d$'arriée Azote Pour Flush ligne produit R35000 |  | JB_Z6_102:3:O.Pt01.Data | JB_Z6_102:12:I.Pt02.Data | JB_Z6_102:12:I.Pt01.Data
XIS_35027 |  | MFG1 |  | Vanne d$'arrivée Azote pour Bullage R35000 |  | JB_Z6_102:3:O.Pt02.Data | JB_Z6_102:12:I.Pt04.Data | JB_Z6_102:12:I.Pt03.Data
XIS_35013 |  | MFG1 |  | Vanne Azote Grand Débit pour Flush Ligne produit R35000 |  | JB_Z6_102:4:O.Pt01.Data | JB_Z6_102:12:I.Pt06.Data | JB_Z6_102:12:I.Pt05.Data
XIS_32041 |  | MFG1 |  | Vanne Azote Grand Débit pour Flush Ligne produit V32000 |  | JB_Z6_102:4:O.Pt02.Data | JB_Z6_102:12:I.Pt08.Data | JB_Z6_102:12:I.Pt07.Data
XIS_32008 |  | MFG1 |  | Vanne d$'arrivée Azote pour Bullage V32000 |  | JB_Z6_102:5:O.Pt01.Data | JB_Z6_102:13:I.Pt02.Data | JB_Z6_102:13:I.Pt01.Data
XIS_32001 |  | MFG1 |  | Vanne d$'arrivée Vapeur Double enveloppe V32000 |  | JB_Z6_102:5:O.Pt02.Data | JB_Z6_102:13:I.Pt04.Data | JB_Z6_102:13:I.Pt03.Data
XIS_32028 |  | MFG1 |  | Vanne d$'arrivée Azote Pour Flush Ligne Produit V32000 |  | JB_Z6_102:6:O.Pt01.Data | JB_Z6_102:13:I.Pt06.Data | JB_Z6_102:13:I.Pt05.Data
XIS_32047 |  | MFG1 |  |  |  | JB_Z6_102:6:O.Pt02.Data | JB_Z6_102:13:I.Pt08.Data | JB_Z6_102:13:I.Pt07.Data
XIS_32048 |  | MFG1 |  |  |  | JB_Z6_102:7:O.Pt01.Data | JB_Z6_102:14:I.Pt02.Data | JB_Z6_102:14:I.Pt01.Data
XIS_32049 |  | MFG1 |  |  |  | JB_Z6_102:7:O.Pt02.Data | JB_Z6_102:14:I.Pt04.Data | JB_Z6_102:14:I.Pt03.Data
XIS_32701 |  | MFG1 |  | Vanne de Fond de Cuve V3200 |  | JB_Z6_102:8:O.Pt01.Data | JB_Z6_102:14:I.Pt06.Data | JB_Z6_102:14:I.Pt05.Data
XIS_33012 |  | MFG1 |  | Vanne Azote pour Flush Ligne produit R33000 |  | JB_Z6_102:8:O.Pt02.Data | JB_Z6_102:14:I.Pt08.Data | JB_Z6_102:14:I.Pt07.Data
XIS_35005 |  | MFG1 |  |  |  | JB_Z6_102:9:O.Pt01.Data | JB_Z6_102:15:I.Pt02.Data | JB_Z6_102:15:I.Pt01.Data
XIS_33063 |  | MFG1 |  |  |  | JB_Z6_102:9:O.Pt02.Data | JB_Z6_102:15:I.Pt04.Data | JB_Z6_102:15:I.Pt03.Data
XIS_34063 |  | MFG1 |  |  |  | JB_Z6_102:10:O.Pt01.Data | JB_Z6_102:15:I.Pt06.Data | JB_Z6_102:15:I.Pt05.Data
XIS_39425 |  | MFG1 |  | Vanne de fond de cuve WT39400 |  | JB_Z6_121_01:1:O.Pt01.Data | JB_Z6_121_01:13:I.Pt02.Data | JB_Z6_121_01:13:I.Pt01.Data
XIS_39424 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Double Enveloppe WT39000 |  | JB_Z6_121_01:1:O.Pt02.Data | JB_Z6_121_01:13:I.Pt04.Data | JB_Z6_121_01:13:I.Pt03.Data
XIS_34204 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E34200 |  | JB_Z6_121_01:2:O.Pt01.Data | JB_Z6_121_01:13:I.Pt06.Data | JB_Z6_121_01:13:I.Pt05.Data
XIS_34053 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R34000 partie Haute |  | JB_Z6_121_01:2:O.Pt02.Data | JB_Z6_121_01:13:I.Pt08.Data | JB_Z6_121_01:13:I.Pt07.Data
XIS_34052 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R34000 partie milieu |  | JB_Z6_121_01:3:O.Pt01.Data | JB_Z6_121_01:14:I.Pt02.Data | JB_Z6_121_01:14:I.Pt01.Data
XIS_34050 |  | MFG1 |  | Vanne Entrée Eau Glacée double enveloppe R34000 partie haute |  | JB_Z6_121_01:3:O.Pt02.Data | JB_Z6_121_01:14:I.Pt04.Data | JB_Z6_121_01:14:I.Pt03.Data
XIS_34019 |  | MFG1 |  | Vanne d$'arrivée Air Comprimé Double Enveloppe R34000 |  | JB_Z6_121_01:4:O.Pt01.Data | JB_Z6_121_01:14:I.Pt06.Data | JB_Z6_121_01:14:I.Pt05.Data
XIS_34017 |  | MFG1 |  | Vanne de retour Eau Glacée R34000 |  | JB_Z6_121_01:4:O.Pt02.Data | JB_Z6_121_01:14:I.Pt08.Data | JB_Z6_121_01:14:I.Pt07.Data
XIS_34015 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée R34000 |  | JB_Z6_121_01:5:O.Pt01.Data | JB_Z6_121_01:15:I.Pt02.Data | JB_Z6_121_01:15:I.Pt01.Data
XIS_34012 |  | MFG1 |  | Vanne de Retour Purge Eau Glacée R34000 |  | JB_Z6_121_01:5:O.Pt02.Data | JB_Z6_121_01:15:I.Pt04.Data | JB_Z6_121_01:15:I.Pt03.Data
XIS_33206 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E33200 |  | JB_Z6_121_01:6:O.Pt01.Data | JB_Z6_121_01:15:I.Pt06.Data | JB_Z6_121_01:15:I.Pt05.Data
XIS_33203 |  | MFG1 |  | Vanne vers Event R33000 |  | JB_Z6_121_01:6:O.Pt02.Data | JB_Z6_121_01:15:I.Pt08.Data | JB_Z6_121_01:15:I.Pt07.Data
XIS_33201 |  | MFG1 |  | Vanne ver Event via PCV R33000 |  | JB_Z6_121_01:7:O.Pt01.Data | JB_Z6_121_01:16:I.Pt02.Data | JB_Z6_121_01:16:I.Pt01.Data
XIS_33053 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R34000 partie Haute |  | JB_Z6_121_01:7:O.Pt02.Data | JB_Z6_121_01:16:I.Pt04.Data | JB_Z6_121_01:16:I.Pt03.Data
XIS_33052 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R34000 partie milieu |  | JB_Z6_121_01:8:O.Pt01.Data | JB_Z6_121_01:16:I.Pt06.Data | JB_Z6_121_01:16:I.Pt05.Data
XIS_33046 |  | MFG1 |  | Vanne d$'arrivée Produit du V3200 vers R33000 |  | JB_Z6_121_01:8:O.Pt02.Data | JB_Z6_121_01:16:I.Pt08.Data | JB_Z6_121_01:16:I.Pt07.Data
SPARE_XIS |  | MFG1 |  |  |  | None | None | None
XIS_33037 |  | MFG1 |  | Vanne de Retour Purge Eau Glacée R33000 |  | JB_Z6_121_02:1:O.Pt02.Data | JB_Z6_121_02:5:I.Pt04.Data | JB_Z6_121_02:5:I.Pt03.Data
XIS_33036 |  | MFG1 |  | Vanne de retour Eau Glacée R33000 |  | JB_Z6_121_02:2:O.Pt01.Data | JB_Z6_121_02:5:I.Pt06.Data | JB_Z6_121_02:5:I.Pt05.Data
XIS_33030 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée R33000 |  | JB_Z6_121_02:2:O.Pt02.Data | JB_Z6_121_02:5:I.Pt08.Data | JB_Z6_121_02:5:I.Pt07.Data
XIS_33027 |  | MFG1 |  | Vanne d$'arrivée Air Comprimé Double Enveloppe R33000 |  | JB_Z6_121_02:3:O.Pt01.Data | JB_Z6_121_02:6:I.Pt02.Data | JB_Z6_121_02:6:I.Pt01.Data
XIS_34033 |  | MFG1 |  |  |  | JB_Z6_121_02:3:O.Pt02.Data | JB_Z6_121_02:6:I.Pt04.Data | JB_Z6_121_02:6:I.Pt03.Data
XIS_32030 |  | MFG1 |  | Vanne d$'arrivée Air Comprimé Double Enveloppe V32000 |  | JB_Z6_122:1:O.Pt01.Data | JB_Z6_122:10:I.Pt02.Data | JB_Z6_122:10:I.Pt01.Data
XIS_32027 |  | MFG1 |  | Vanne de purge Eau Glacée Double enveloppe V32000 |  | JB_Z6_122:1:O.Pt02.Data | JB_Z6_122:10:I.Pt04.Data | JB_Z6_122:10:I.Pt03.Data
XIS_32026 |  | MFG1 |  | Vanne de Retour Eau Glacée Double Enveloppe V32000 |  | JB_Z6_122:2:O.Pt01.Data | JB_Z6_122:10:I.Pt06.Data | JB_Z6_122:10:I.Pt05.Data
XIS_32023 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Double Enveloppe V32000 |  | JB_Z6_122:2:O.Pt02.Data | JB_Z6_122:10:I.Pt08.Data | JB_Z6_122:10:I.Pt07.Data
XIS_32018 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condesneur E32200 |  | JB_Z6_122:3:O.Pt01.Data | JB_Z6_122:11:I.Pt02.Data | JB_Z6_122:11:I.Pt01.Data
XIS_31033 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Double Enveloppe R31000 |  | JB_Z6_122:3:O.Pt02.Data | JB_Z6_122:11:I.Pt04.Data | JB_Z6_122:11:I.Pt03.Data
XIS_31007 |  | MFG1 |  | Vanne D$'arrivée Vapeur Double Enveloppe R31000 |  | JB_Z6_122:4:O.Pt01.Data | JB_Z6_122:11:I.Pt06.Data | JB_Z6_122:11:I.Pt05.Data
XIS_31006 |  | MFG1 |  | Vanne d$'arrivée Air Comprimé Double Enveloppe R31000 |  | JB_Z6_122:4:O.Pt02.Data | JB_Z6_122:11:I.Pt08.Data | JB_Z6_122:11:I.Pt07.Data
XIS_31005 |  | MFG1 |  | Vanne de Purge Condensat partie haute Double Enveloppe R31000 |  | JB_Z6_122:5:O.Pt01.Data | JB_Z6_122:12:I.Pt02.Data | JB_Z6_122:12:I.Pt01.Data
XIS_31087 |  | MFG1 |  | Vanne de Purge Condensat partie Basse Double Enveloppe R31000 |  | JB_Z6_122:5:O.Pt02.Data | JB_Z6_122:12:I.Pt04.Data | JB_Z6_122:12:I.Pt03.Data
XIS_31086 |  | MFG1 |  | Vanne Choix partie Haute double Enveloppe R31000 |  | JB_Z6_122:6:O.Pt01.Data | JB_Z6_122:12:I.Pt06.Data | JB_Z6_122:12:I.Pt05.Data
XIS_31085 |  | MFG1 |  | Vanne Choix partie Milieu double Enveloppe R31000 |  | JB_Z6_122:6:O.Pt02.Data | JB_Z6_122:12:I.Pt08.Data | JB_Z6_122:12:I.Pt07.Data
XIS_32050 |  | MFG1 |  |  |  | JB_Z6_122:7:O.Pt01.Data | JB_Z6_122:13:I.Pt02.Data | JB_Z6_122:13:I.Pt01.Data
XIS_31083 |  | MFG1 |  | Vanne Choix partie Milieu double Enveloppe R31000 |  | JB_Z6_122:7:O.Pt02.Data | JB_Z6_122:13:I.Pt04.Data | JB_Z6_122:13:I.Pt03.Data
XIS_31043 |  | MFG1 |  | Vanne de purge Eau Glacée Double enveloppe R31000 |  | JB_Z6_122:8:O.Pt01.Data | JB_Z6_122:13:I.Pt06.Data | JB_Z6_122:13:I.Pt05.Data
XIS_35023 |  | MFG1 |  | Vanne d$'arrivée Ait comprimé vers Double Enveloppe R35000 |  | JB_Z6_122:8:O.Pt02.Data | JB_Z6_122:13:I.Pt08.Data | JB_Z6_122:13:I.Pt07.Data
XIS_35053 |  | MFG1 |  | Vanne Sortie Eau Glacée double enveloppe R35000 partie Haute |  | JB_Z6_122:9:O.Pt01.Data | JB_Z6_122:14:I.Pt02.Data | JB_Z6_122:14:I.Pt01.Data
XIS_32044 |  | MFG1 |  | Vanne Sortie Cuve V32000 vers Event |  | JB_Z6_131:1:O.Pt01.Data | JB_Z6_131:4:I.Pt02.Data | JB_Z6_131:4:I.Pt01.Data
XIS_32043 |  | MFG1 |  | Vanne Sortie Cuve V32000 vers Event via PCV |  | JB_Z6_131:1:O.Pt02.Data | JB_Z6_131:4:I.Pt04.Data | JB_Z6_131:4:I.Pt03.Data
XIS_31008 |  | MFG1 |  | Vanne Choix partie Basse double Enveloppe R31000 |  | JB_Z6_131:2:O.Pt01.Data | JB_Z6_131:4:I.Pt06.Data | JB_Z6_131:4:I.Pt05.Data
XIS_39861 |  | MFG1 |  | Vanne d$'envoie produit de WT39700 vers R35000 |  | JB_Z6_132:1:O.Pt01.Data | JB_Z6_132:12:I.Pt02.Data | JB_Z6_132:12:I.Pt01.Data
XIS_39860 |  | MFG1 |  | Vanne d$'envoie produit de WT39700 vers R33000 |  | JB_Z6_132:1:O.Pt02.Data | JB_Z6_132:12:I.Pt04.Data | JB_Z6_132:12:I.Pt03.Data
XIS_39859 |  | MFG1 |  | Vanne d$'envoie produit de WT39700 vers R34000 |  | JB_Z6_132:2:O.Pt01.Data | JB_Z6_132:12:I.Pt06.Data | JB_Z6_132:12:I.Pt05.Data
XIS_39858 |  | MFG1 |  | Vanne d$'envoie vers de WT39700 Process Q38 - R33000 et R34000 |  | JB_Z6_132:2:O.Pt02.Data | JB_Z6_132:12:I.Pt08.Data | JB_Z6_132:12:I.Pt07.Data
XIS_39725 |  | MFG1 |  | Vanne de Fond de Cuve WT39700 |  | JB_Z6_132:3:O.Pt01.Data | JB_Z6_132:13:I.Pt02.Data | JB_Z6_132:13:I.Pt01.Data
XIS_39724 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Double Enveloppe WT39700 |  | JB_Z6_132:3:O.Pt02.Data | JB_Z6_132:13:I.Pt04.Data | JB_Z6_132:13:I.Pt03.Data
XIS_39561 |  | MFG1 |  | Vanne d$'envoie produit vers de WT39400 R35000 |  | JB_Z6_132:4:O.Pt01.Data | JB_Z6_132:13:I.Pt06.Data | JB_Z6_132:13:I.Pt05.Data
XIS_39560 |  | MFG1 |  | Vanne d$'envoie produit vers de WT39400 R33000 |  | JB_Z6_132:4:O.Pt02.Data | JB_Z6_132:13:I.Pt08.Data | JB_Z6_132:13:I.Pt07.Data
XIS_39559 |  | MFG1 |  | Vanne d$'envoie produit vers de WT39400 R34000 |  | JB_Z6_132:5:O.Pt01.Data | JB_Z6_132:14:I.Pt02.Data | JB_Z6_132:14:I.Pt01.Data
XIS_39558 |  | MFG1 |  | Vanne d$'envoie vers de WT39400 Process Q38 - R33000 et R34000 |  | JB_Z6_132:5:O.Pt02.Data | JB_Z6_132:14:I.Pt04.Data | JB_Z6_132:14:I.Pt03.Data
XIS_34201 |  | MFG1 |  | Vanne Event via PCV R34000 |  | JB_Z6_132:6:O.Pt01.Data | JB_Z6_132:14:I.Pt08.Data | JB_Z6_132:14:I.Pt07.Data
XIS_34202 |  | MFG1 |  | Vanne Event R34000 |  | JB_Z6_132:6:O.Pt02.Data | JB_Z6_132:14:I.Pt06.Data | JB_Z6_132:14:I.Pt05.Data
XIS_35020 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Vers Double Enveloppe R35000 |  | JB_Z6_132:7:O.Pt01.Data | JB_Z6_132:15:I.Pt02.Data | JB_Z6_132:15:I.Pt01.Data
XIS_35037 |  | MFG1 |  | Vanne Retour Eau Glacée R35000 |  | JB_Z6_132:7:O.Pt02.Data | JB_Z6_132:15:I.Pt04.Data | JB_Z6_132:15:I.Pt03.Data
XIS_35038 |  | MFG1 |  | Vanne Retour Eau Glacée pour vidange double enveloppe R35000 |  | JB_Z6_132:8:O.Pt01.Data | JB_Z6_132:15:I.Pt06.Data | JB_Z6_132:15:I.Pt05.Data
XIS_35208 |  | MFG1 |  | Vanne Sortie Cuve R35000 vers Event via PCV |  | JB_Z6_132:8:O.Pt02.Data | JB_Z6_132:15:I.Pt08.Data | JB_Z6_132:15:I.Pt07.Data
XIS_35205 |  | MFG1 |  | Vanne D$'arrivée Eau Glacée vers Condenseur E35200 |  | JB_Z6_132:9:O.Pt01.Data | JB_Z6_132:16:I.Pt02.Data | JB_Z6_132:16:I.Pt01.Data
XIS_35201 |  | MFG1 |  | Vanne Sortie Cuve R35000 vers Event |  | JB_Z6_132:9:O.Pt02.Data | JB_Z6_132:16:I.Pt04.Data | JB_Z6_132:16:I.Pt03.Data
XIS_30025 |  | MFG1 |  | Vanne de Fond De Cuve WT30000 |  | JB_Z6_141:1:O.Pt01.Data | JB_Z6_141:11:I.Pt08.Data | JB_Z6_141:11:I.Pt07.Data
XIS_92003 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Pompe à vide |  | JB_Z6_141:1:O.Pt02.Data | JB_Z6_141:11:I.Pt04.Data | JB_Z6_141:11:I.Pt03.Data
XIS_31212 |  | MFG1 |  | Vanne de purge sous Condenseur E31200 |  | JB_Z6_141:2:O.Pt01.Data | JB_Z6_141:11:I.Pt06.Data | JB_Z6_141:11:I.Pt05.Data
XIS_31205 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E31200 |  | JB_Z6_141:2:O.Pt02.Data | JB_Z6_141:11:I.Pt02.Data | JB_Z6_141:11:I.Pt01.Data
XIS_31210 |  | MFG1 |  | Vanne d$'isolement consenseur E31200 / R31000 |  | JB_Z6_141:3:O.Pt01.Data | JB_Z6_141:12:I.Pt02.Data | JB_Z6_141:12:I.Pt01.Data
XIS_31211 |  | MFG1 |  | Vanne d$'arrivée BG vers Condenseur E31200 |  | JB_Z6_141:3:O.Pt02.Data | JB_Z6_141:12:I.Pt04.Data | JB_Z6_141:12:I.Pt03.Data
XIS_31505 |  | MFG1 |  | Vanne Sortie Event Cuve V31500 |  | JB_Z6_141:4:O.Pt01.Data | JB_Z6_141:12:I.Pt06.Data | JB_Z6_141:12:I.Pt05.Data
XIS_31502 |  | MFG1 |  | Vanne arrivée ETPPI De Cuve V31500 ver R31000 |  | JB_Z6_141:4:O.Pt02.Data | JB_Z6_141:12:I.Pt08.Data | JB_Z6_141:12:I.Pt07.Data
XIS_31501 |  | MFG1 |  | Vanne d$'arrivée Produit V31500 |  | JB_Z6_141:5:O.Pt01.Data | JB_Z6_141:13:I.Pt02.Data | JB_Z6_141:13:I.Pt01.Data
XIS_31306 |  | MFG1 |  | Vanne d$'arrivé air sur Pompe P31300 |  | JB_Z6_141:5:O.Pt02.Data | JB_Z6_141:13:I.Pt04.Data | JB_Z6_141:13:I.Pt03.Data
XIS_31039 |  | MFG1 |  | Vanne d$'arrivée Azote Cuve V31500 |  | JB_Z6_141:6:O.Pt01.Data | JB_Z6_141:13:I.Pt06.Data | JB_Z6_141:13:I.Pt05.Data
XIS_31056 |  | MFG1 |  | Vanne d$'arrivée Azote R31000 |  | JB_Z6_141:6:O.Pt02.Data | JB_Z6_141:13:I.Pt08.Data | JB_Z6_141:13:I.Pt07.Data
XIS_31015 |  | MFG1 |  | Vanne d$'arrivée Produit Du IBC TE0038 vers R31000 |  | JB_Z6_141:7:O.Pt01.Data | JB_Z6_141:14:I.Pt02.Data | JB_Z6_141:14:I.Pt01.Data
XIS_31059 |  | MFG1 |  | Vanne Bypass PCV Sur ligne arrivée Azote R31000 |  | JB_Z6_141:7:O.Pt02.Data | JB_Z6_141:14:I.Pt04.Data | JB_Z6_141:14:I.Pt03.Data
XIS_39904 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E39900 |  | JB_Z6_141:8:O.Pt01.Data | JB_Z6_141:14:I.Pt06.Data | JB_Z6_141:14:I.Pt05.Data
XIS_39735 |  | MFG1 |  | Vanne de Bypass PCV Ligne d$'arrivée Gaz Vers WT39700 |  | JB_Z6_141:8:O.Pt02.Data | JB_Z6_141:14:I.Pt08.Data | JB_Z6_141:14:I.Pt07.Data
XIS_39602 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E39600 |  | JB_Z6_141:9:O.Pt01.Data | JB_Z6_141:15:I.Pt02.Data | JB_Z6_141:15:I.Pt01.Data
XIS_39437 |  | MFG1 |  | Vanne de Bypass PCV Ligne d$'arrivée Gaz Vers WT39400 |  | JB_Z6_141:9:O.Pt02.Data | JB_Z6_141:15:I.Pt04.Data | JB_Z6_141:15:I.Pt03.Data
XIS_30604 |  | MFG1 |  |  |  | JB_Z6_141:10:O.Pt01.Data | JB_Z6_141:15:I.Pt05.Data | JB_Z6_141:15:I.Pt06.Data
XIS_31073 |  | MFG1 |  |  |  | JB_Z6_141:10:O.Pt02.Data | JB_Z6_141:15:I.Pt08.Data | JB_Z6_141:15:I.Pt07.Data
XIS_39737 |  | MFG1 |  | Vanne d$'event WT39700 |  | JB_Z6_161:1:O.Pt01.Data | JB_Z6_161:10:I.Pt02.Data | JB_Z6_161:10:I.Pt01.Data
XIS_39736 |  | MFG1 |  | Vanne d$'event via PCV WT39700 |  | JB_Z6_161:1:O.Pt02.Data | JB_Z6_161:10:I.Pt04.Data | JB_Z6_161:10:I.Pt03.Data
XIS_39440 |  | MFG1 |  | Vanne d$'event via PCV WT39400 |  | JB_Z6_161:2:O.Pt01.Data | JB_Z6_161:10:I.Pt06.Data | JB_Z6_161:10:I.Pt05.Data
XIS_31204 |  | MFG1 |  | Vanne d$'event R31000 |  | JB_Z6_161:2:O.Pt02.Data | JB_Z6_161:10:I.Pt08.Data | JB_Z6_161:10:I.Pt07.Data
XIS_31202 |  | MFG1 |  | Vanne d$'event via PCV R31000 |  | JB_Z6_161:3:O.Pt01.Data | JB_Z6_161:11:I.Pt02.Data | JB_Z6_161:11:I.Pt01.Data
XIS_31075 |  | MFG1 |  | Vanne de recirculation DGE vers T88000 |  | JB_Z6_161:3:O.Pt02.Data | JB_Z6_161:11:I.Pt04.Data | JB_Z6_161:11:I.Pt03.Data
XIS_31074 |  | MFG1 |  | Vanne d$'arrivée DGE vers R31000 |  | JB_Z6_161:4:O.Pt01.Data | JB_Z6_161:11:I.Pt06.Data | JB_Z6_161:11:I.Pt05.Data
XIS_30207 |  | MFG1 |  | Vanne d$'event WT30000 |  | JB_Z6_161:4:O.Pt02.Data | JB_Z6_161:11:I.Pt08.Data | JB_Z6_161:11:I.Pt07.Data
XIS_30206 |  | MFG1 |  | Vanne d$'event via PCV WT30000 |  | JB_Z6_161:5:O.Pt01.Data | JB_Z6_161:12:I.Pt02.Data | JB_Z6_161:12:I.Pt01.Data
XIS_30204 |  | MFG1 |  | Vanne d$'arrivée Eau Glacée Condenseur E30200 |  | JB_Z6_161:5:O.Pt02.Data | JB_Z6_161:12:I.Pt04.Data | JB_Z6_161:12:I.Pt03.Data
XIS_30013 |  | MFG1 |  | Vanne d$'arrivée Acrylic T87000 vers WT30000 |  | JB_Z6_161:6:O.Pt01.Data | JB_Z6_161:12:I.Pt06.Data | JB_Z6_161:12:I.Pt05.Data
XIS_30012 |  | MFG1 |  | Vanne d$'arrivée Acrylic T86000 vers WT30000 |  | JB_Z6_161:6:O.Pt02.Data | JB_Z6_161:12:I.Pt08.Data | JB_Z6_161:12:I.Pt07.Data
XIS_30002 |  | MFG1 |  | Vanne de Bypass PCV alimentation Azote WT30000 |  | JB_Z6_161:7:O.Pt01.Data | JB_Z6_161:13:I.Pt02.Data | JB_Z6_161:13:I.Pt01.Data
XIS_39439 |  | MFG1 |  | Vanne vers Event WT39400 |  | JB_Z6_161:7:O.Pt02.Data | JB_Z6_161:13:I.Pt04.Data | JB_Z6_161:13:I.Pt03.Data
XIS_31213 |  | MFG1 |  | Vanne de sortie Condenseur E31200 |  | JB_Z6_161:8:O.Pt01.Data | JB_Z6_161:13:I.Pt06.Data | JB_Z6_161:13:I.Pt05.Data
XIS_31036 |  | MFG1 |  | Vanne de Retour Eau Glacée R31000 |  | JB_Z6_161:8:O.Pt02.Data | JB_Z6_161:13:I.Pt08.Data | JB_Z6_161:13:I.Pt07.Data
XIS_31084 |  | MFG1 |  | Vanne Choix partie Haute double Enveloppe R31000 |  | JB_Z6_161:9:O.Pt01.Data | JB_Z6_161:14:I.Pt02.Data | JB_Z6_161:14:I.Pt01.Data
XIS_91605 |  | MFG1 |  | Vanne de Recirculation Eau Chaude Osmosée T91500 |  | JB_Z7_101:1:O.Pt01.Data | JB_Z7_101:7:I.Pt02.Data | JB_Z7_101:7:I.Pt01.Data
XIS_91509 |  | MFG1 |  | Vanne d$'alimentation Eau Osmosée ver T91500 |  | JB_Z7_101:1:O.Pt02.Data | JB_Z7_101:7:I.Pt04.Data | JB_Z7_101:7:I.Pt03.Data
XIS_91008 |  | MFG1 |  | Vanne d$'alimentation Eau Osmosée ver T91500 |  | JB_Z7_101:2:O.Pt01.Data | JB_Z7_101:7:I.Pt06.Data | JB_Z7_101:7:I.Pt05.Data
XIS_90004 |  | MFG1 |  | Vanne de fond de cuve T91000 |  | JB_Z7_101:2:O.Pt02.Data | JB_Z7_101:7:I.Pt08.Data | JB_Z7_101:7:I.Pt07.Data
XIS_90005 |  | MFG1 |  |  |  | JB_Z7_101:3:O.Pt01.Data | JB_Z7_101:8:I.Pt02.Data | JB_Z7_101:8:I.Pt01.Data
XIS_91005 |  | MFG1 |  |  |  | JB_Z7_101:3:O.Pt02.Data | JB_Z7_101:8:I.Pt04.Data | JB_Z7_101:8:I.Pt03.Data
XIS_91203 |  | MFG1 |  |  |  | JB_Z7_101:4:O.Pt01.Data | JB_Z7_101:8:I.Pt06.Data | JB_Z7_101:8:I.Pt05.Data
XIS_97933 |  | MFG1 |  |  |  | JB_Z7_101:4:O.Pt02.Data | JB_Z7_101:8:I.Pt08.Data | JB_Z7_101:8:I.Pt07.Data
XIS_92001 |  | MFG1 |  | Vacuum Valve |  | None | None | None
XIS_92004 |  | MFG1 |  | Vacuum Valve |  | None | None | None
XIS_80004 |  | BULK
XIS_85502 |  | BULK |  | Vanne d'arrivée Eau Glacée Echangeur E85500
XIS_85012 |  | BULK |  | Vanne de recirculation T85000
XIS_84501 |  | BULK |  | Vanne d'arrivée Eau Glacée Echangeur E84500
XIS_84005 |  | BULK |  | Vanne de recirculation T84000
XIS_83502 |  | BULK |  | Vanne d'arrivée Eau Glacée Echangeur E83500
XIS_83012 |  | BULK |  | Vanne de recirculation T83000
XIS_82502 |  | BULK |  | Vanne d'arrivée Eau Glacée Echangeur E82500
XIS_82012 |  | BULK |  | Vanne de recirculation T82000
XIS_42033 |  | BULK |  | Vanne d'arrivée d'eau vers Boule de Lavage V42000
XIS_40050 |  | BULK |  | Vanne d'arrivée DMEA de R007 vers V40000
XIS_42005 |  | BULK |  | Vanne d'arrivée DMEA de R007 vers V42000
XIS_42004 |  | BULK |  | Vanne d'arrivée Eau vers V42000
XIS_42003 |  | BULK |  | Vanne d'arrivée BG Vers V42000
XIS_42002 |  | BULK |  | Vanne d'arrivée Amyl Alcool Vers V42000
XIS_41027 |  | BULK |  | Vanne d'arrivée d'eau vers Boule de Lavage V41000
XIS_41025 |  | BULK |  | Vanne d'arrivée Mélange Static Mixer SM41500 vers V41000
XIS_41005 |  | BULK |  | Vanne d'rrivée Buthanol ou Amyl Alcool vers V41000
XIS_41004 |  | BULK |  | Vanne d'arrivée DMEA de R007 vers V41000
XIS_40051 |  | BULK |  | Vanne d'arrivée AmyL Ou Buthanol Vers V40000
XIS_40037 |  | BULK |  | Vanne d'arrivée Eau vers Static Mixer SM41500
XIS_40022 |  | BULK |  | Vanne d'arrivée d'eau vers Boule de Lavage V40000
XIS_40019 |  | BULK |  | Vanne d'arrivée Mélange Static Mixer SM41500 vers V40000
XIS_40016 |  | BULK |  | Vanne d'rrivée Buthanol ou Amyl Alcool vers V40000
XIS_40015 |  | BULK |  | Vanne d'arrivée DMEA de R007 vers V40000
XIS_40052 |  | BULK |  | Vanne d'arrivée Mélange Static Mixer SM41500 Dans V40000
XIS_40003 |  | BULK |  | Vanne d'arrivée BG Vers Static Mixer S41500
XIS_40002 |  | BULK |  | Vanne d'arrivée Amyl Alcool vers V40000 et V41000
XIS_40001 |  | BULK |  | Vanne d'arrivée Buthanol vers V40000 et V41000
XIS_41050 |  | BULK |  | Vanne d'arrivée DMEA de R007 Dans V41000
XIS_41051 |  | BULK |  | Vanne d'arrivée AmyL Ou Buthanol Dans V41000
XIS_41052 |  | BULK |  | Vanne d'arrivée Mélange Static Mixer SM41500 Dans V41000
XIS_35061 |  | BULK
XIS_35062 |  | BULK
XIS_35063 |  | BULK
XIS_99502 |  | BULK |  | Vanne d'arrivée Air pour Pompe P99500 vers Pico T99000
XIS_99006 |  | BULK |  | Vanne d'arrivée Eau Osmosée vers T99000
XIS_99307 |  | BULK
XIS_47506 |  | BULK
XIS_47501 |  | BULK
XIS_31037 |  | BULK |  | Vanne d'envoie vers IBC de rejet
XIS_35028 |  | BULK |  | Vanne d'arrivée produit de R31000 vers R35000
XIS_32009 |  | BULK |  | Vanne d'arrivée produit de R31000 vers V32000
XIS_31408 |  | BULK |  | Vanne isolation après Filtre F31600
XIS_31407 |  | BULK |  | Vanne isolation avant Filtre F31600
XIS_31406 |  | BULK |  | Vanne d'envoie BG vers Condenseur E31200
XIS_31405 |  | BULK |  | Vanne recirculation BG après Filtre F31600
XIS_33061 |  | BULK
XIS_33062 |  | BULK
XIS_34061 |  | BULK
XIS_34062 |  | BULK
XIS_34064 |  | BULK
XIS_33001 |  | BULK |  | Vanne d'arrivée DMEA R007 dans R33000
XIS_31050 |  | BULK |  | Vanne d'envoie produit de R31000 vers Pompe P31400 recirculation ou IBC
XIS_31012 |  | BULK |  | Vanne d'envoie produit de R31000 vers Cuve Pico T99000
XIS_31701 |  | BULK |  | Vanne de Fond de cuve R31000
XIS_39206 |  | BULK |  | Vanne d'arrivée Air Sur Pompe P39200
XIS_31065 |  | BULK
XIS_33065 |  | BULK
XIS_33066 |  | BULK
XIS_33067 |  | BULK
XIS_39034 |  | BULK
XIS_39035 |  | BULK
XIS_31088 |  | BULK
XIS_39734 |  | BULK |  | Vanne d'arrivée Eau WT39700
XIS_39420 |  | BULK |  | Vanne d'arrivée Eau WT39400
XIS_39156 |  | BULK |  | Vanne d'arrivée Air Sur Pompe P39150
XIS_39030 |  | BULK |  | Vanne d'envoie de WT39000 vers R34000
XIS_39029 |  | BULK |  | Vanne d'envoie de H202 IBC vers R34000
XIS_39015 |  | BULK |  | Vanne d'arrivée Eau vers WT39000
XIS_39013 |  | BULK |  | Vanne d'envoie de WT39000 vers R33000 / R34000
XIS_39012 |  | BULK |  | Vanne d'envoie de H202 IBC vers R33000 / R34000
XIS_39011 |  | BULK |  | Vanne d'envoie de WT39000 vers R33000
XIS_39010 |  | BULK |  | Vanne d'envoie de H202 IBC vers R33000
XIS_39007 |  | BULK |  | Vanne de Fond de Cuve WT39000
XIS_39005 |  | BULK |  | Vanne d'envoie de WT39000 vers R35000
XIS_39004 |  | BULK |  | Vanne d'envoie de H202 IBC vers R35000
XIS_31032 |  | BULK |  | Vanne d'arrivée Eau Osmosée dans R31000
XIS_31026 |  | BULK |  | Vanne arrivée eau chaude pour Flush ligne produit R31000
XIS_31011 |  | BULK |  | Vanne d'arrivée DMEA R007 dans R31000
XIS_31064 |  | BULK |  | Vanne d'arrivée Pico vers R31000
XIS_31047 |  | BULK |  | Vanne d'envoie BG vers R31000 via boule de lavage
XIS_35046 |  | BULK |  | Vanne d'arrivée Eau Chaude Osmosée vers R35000
XIS_39032 |  | BULK
XIS_89551 |  | BULK |  | Vanne d'arrivée Air Sur Pompe P89550
XIS_39355 |  | BULK |  | Vanne d'arrivée Air Sur Pompe P39350
XIS_35060 |  | BULK |  | Vanne d'arrivée Eau Osmosée via Boule de lavage R35000
XIS_35011 |  | BULK |  | Vanne d'arrivée Eau Osmosée vers R35000
XIS_35010 |  | BULK |  | Vanne d'arrivée Benzoine WT39000 vers R35000
XIS_34044 |  | BULK |  | Vanne d'arrivée Eau Chaude Osmosée via Boule de lavage R34000
XIS_35058 |  | BULK |  | Vanne d'arrivée Eau Osmosée Mélangée dans R35000
XIS_34014 |  | BULK |  | Vanne d'arrivée Eau Chaude Osmosée dans R34000
XIS_33009 |  | BULK |  | Vanne d'envoie Eau Osmosée dans R34000
XIS_33008 |  | BULK |  | Vanne d'arrivée Eau Osmosée dans R33000
XIS_33005 |  | BULK |  | Vanne d'arrivée Eau Osmosée Tiède dans R33000 /R34000
XIS_33004 |  | BULK |  | Vanne d'arrivée Eau Osmosée Froide dans R33000 /R34000
XIS_32011 |  | BULK |  | Vanne d'arrivée Eau Chaude Osmosée dans V32000
XIS_32034 |  | BULK |  | Vanne d'arrivée Eau Chaude Osmosée via Boule de lavage V32000
XIS_39732 |  | BULK |  | Vanne d'arrivée Produit Dans WT39700
XIS_30015 |  | BULK |  | Vanne d'arrivée BG vers WT30000
XIS_39418 |  | BULK |  | Vanne d'arrivée Produit Dans WT39400
XIS_39414 |  | BULK |  | Vanne d'arrivée produit du T85000 vers WT39400/39700
XIS_39413 |  | BULK |  | Vanne d'arrivée produit du T84000 vers WT39400/39700
XIS_39412 |  | BULK |  | Vanne d'arrivée produit du T83000 vers WT39400/39700
XIS_39411 |  | BULK |  | Vanne d'arrivée produit du T82000 vers WT39400/39700
XIS_31014 |  | BULK |  | Vanne d'arrivée BG vers R31000
XIS_31072 |  | BULK |  | Vanne d'arrivée BG/Buthanol dans R31000
XIS_31055 |  | BULK |  | Vanne d'arrivée Buthanol vers R31000
XIS_89351 |  | BULK |  | Vanne d'envoie de R006 vers process V70
XIS_89251 |  | BULK |  | Vanne d'envoie de R007 vers process V70
XIS_81301 |  | BULK |  | Vanne d'envoie de R005 vers process V70
XIS_39357 |  | BULK |  | Pico DLY Valve
XIS_39428 |  | BULK |  | WT39400 RO Water SprayBalls
XIS_39738 |  | BULK |  | WT39700 RO Water SprayBalls
XIS_31079 |  | BULK |  | R31000 to V32000 DLY Valve BLK
XIS_80014 |  | LUL |  | CM_V2W
XIS_82008 |  | LUL |  | CM_V2W
XIS_83002 |  | LUL |  | CM_V2W
XIS_84001 |  | LUL |  | CM_V2W
XIS_85019 |  | LUL |  | CM_V2W
XIS_43005 |  | LUL |  | CM_V2W
XIS_43014 |  | LUL |  | CM_V2W
XIS_43015 |  | LUL |  | CM_V2W
XIS_43018 |  | LUL |  | CM_V2W
XIS_44005 |  | LUL |  | CM_V2W
XIS_44011 |  | LUL |  | CM_V2W
XIS_44015 |  | LUL |  | CM_V2W
XIS_44018 |  | LUL |  | CM_V2W
XIS_45004 |  | LUL |  | CM_V2W
XIS_45013 |  | LUL |  | CM_V2W
XIS_45014 |  | LUL |  | CM_V2W
XIS_45015 |  | LUL |  | CM_V2W
XIS_86002 |  | LUL |  | CM_V2W
XIS_87005 |  | LUL |  | CM_V2W
XIS_88020 |  | LUL |  | CM_V2W
XIS_46001 |  | LUL |  | CM_V2W
XIS_46003 |  | LUL |  | CM_V2W
XIS_46004 |  | LUL |  | CM_V2W
XIS_46006 |  | LUL |  | CM_V2W
XIS_46007 |  | LUL |  | CM_V2W
XIS_47001 |  | LUL |  | CM_V2W
XIS_47002 |  | LUL |  | CM_V2W
XIS_47003 |  | LUL |  | CM_V2W
XIS_47004 |  | LUL |  | CM_V2W
XIS_47007 |  | LUL |  | CM_V2W
XIS_89101 |  | LUL |  | CM_V2W
XIS_89102 |  | LUL |  | CM_V2W
XIS_89202 |  | LUL |  | CM_V2W
XIS_89302 |  | LUL |  | CM_V2W
XIS_89402 |  | LUL |  | CM_V2W
XIS_89501 |  | LUL |  | CM_V2W
XIS_89502 |  | LUL |  | CM_V2W
XIS_89601 |  | LUL |  | CM_V2W
XIS_89602 |  | LUL |  | CM_V2W
XIS_89702 |  | LUL |  | CM_V2W
XIS_89802 |  | LUL |  | CM_V2W
XIS_96201 |  | SIS |  | CM_V2W
XIS_96202 |  | SIS |  | CM_V2W
XIS_96209 |  | SIS |  | CM_V2W
XIS_80012 |  | SIS |  | CM_V2W
XIS_80018 |  | SIS |  | CM_V2W
XIS_82015 |  | SIS |  | CM_V2W
XIS_82042 |  | SIS |  | CM_V2W
XIS_82043 |  | SIS |  | CM_V2W
XIS_83013 |  | SIS |  | CM_V2W
XIS_83042 |  | SIS |  | CM_V2W
XIS_83043 |  | SIS |  | CM_V2W
XIS_84002 |  | SIS |  | CM_V2W
XIS_84042 |  | SIS |  | CM_V2W
XIS_84043 |  | SIS |  | CM_V2W
XIS_85017 |  | SIS |  | CM_V2W
XIS_85042 |  | SIS |  | CM_V2W
XIS_85043 |  | SIS |  | CM_V2W
XIS_82041 |  | SIS |  | CM_V2W
XIS_83041 |  | SIS |  | CM_V2W
XIS_84041 |  | SIS |  | CM_V2W
XIS_85041 |  | SIS |  | CM_V2W
XIS_82001 |  | SIS |  | CM_V2W
XIS_82013 |  | SIS |  | CM_V2W
XIS_83001 |  | SIS |  | CM_V2W
XIS_83016 |  | SIS |  | CM_V2W
XIS_84013 |  | SIS |  | CM_V2W
XIS_84016 |  | SIS |  | CM_V2W
XIS_85013 |  | SIS |  | CM_V2W
XIS_85016 |  | SIS |  | CM_V2W
XIS_40030 |  | SIS |  | CM_V2W
XIS_40308 |  | SIS |  | CM_V2W
XIS_41020 |  | SIS |  | CM_V2W
XIS_42027 |  | SIS |  | CM_V2W
XIS_86009 |  | SIS |  | CM_V2W
XIS_86013 |  | SIS |  | CM_V2W
XIS_86016 |  | SIS |  | CM_V2W
XIS_86201 |  | SIS |  | CM_V2W
XIS_87003 |  | SIS |  | CM_V2W
XIS_87012 |  | SIS |  | CM_V2W
XIS_87014 |  | SIS |  | CM_V2W
XIS_87201 |  | SIS |  | CM_V2W
XIS_88012 |  | SIS |  | CM_V2W
XIS_88014 |  | SIS |  | CM_V2W
XIS_88015 |  | SIS |  | CM_V2W
XIS_88201 |  | SIS |  | CM_V2W
XIS_32010 |  | SIS |  | CM_V2W
XIS_32012 |  | SIS |  | CM_V2W
XIS_32306 |  | SIS |  | CM_V2W
XIS_33034 |  | SIS |  | CM_V2W
XIS_33040 |  | SIS |  | CM_V2W
XIS_33307 |  | SIS |  | CM_V2W
XIS_34004 |  | SIS |  | CM_V2W
XIS_34013 |  | SIS |  | CM_V2W
XIS_34027 |  | SIS |  | CM_V2W
XIS_34307 |  | SIS |  | CM_V2W
XIS_35001 |  | SIS |  | CM_V2W
XIS_35004 |  | SIS |  | CM_V2W
XIS_35035 |  | SIS |  | CM_V2W
XIS_40201 |  | SIS |  | CM_V2W
XIS_41201 |  | SIS |  | CM_V2W
XIS_42201 |  | SIS |  | CM_V2W
XIS_47505 |  | SIS |  | CM_V2W
XIS_99002 |  | SIS |  | CM_V2W
XIS_99004 |  | SIS |  | CM_V2W
XIS_99302 |  | SIS |  | CM_V2W
XIS_99501 |  | SIS |  | CM_V2W
XIS_31041 |  | SIS |  | CM_V2W
XIS_31077 |  | SIS |  | CM_V2W
XIS_31078 |  | SIS |  | CM_V2W
XIS_33015 |  | SIS |  | CM_V2W
XIS_34030 |  | SIS |  | CM_V2W
XIS_35047 |  | SIS |  | CM_V2W
XIS_39033 |  | SIS |  | CM_V2W
XIS_39207 |  | SIS |  | CM_V2W
XIS_31029 |  | SIS |  | CM_V2W
XIS_32002 |  | SIS |  | CM_V2W
XIS_32021 |  | SIS |  | CM_V2W
XIS_33010 |  | SIS |  | CM_V2W
XIS_33011 |  | SIS |  | CM_V2W
XIS_33014 |  | SIS |  | CM_V2W
XIS_34024 |  | SIS |  | CM_V2W
XIS_35003 |  | SIS |  | CM_V2W
XIS_35008 |  | SIS |  | CM_V2W
XIS_39031 |  | SIS |  | CM_V2W
XIS_39157 |  | SIS |  | CM_V2W
XIS_30003 |  | SIS |  | CM_V2W
XIS_30024 |  | SIS |  | CM_V2W
XIS_31019 |  | SIS |  | CM_V2W
XIS_31024 |  | SIS |  | CM_V2W
XIS_31053 |  | SIS |  | CM_V2W
XIS_31073 |  | SIS |  | CM_V2W
XIS_31301 |  | SIS |  | CM_V2W
XIS_39008 |  | SIS |  | CM_V2W
XIS_39358 |  | SIS |  | CM_V2W
XIS_39427 |  | SIS |  | CM_V2W
XIS_39442 |  | SIS |  | CM_V2W
XIS_39443 |  | SIS |  | CM_V2W
XIS_39435 |  | SIS |  | CM_V2W
XIS_39727 |  | SIS |  | CM_V2W
XIS_39742 |  | SIS |  | CM_V2W
XIS_39743 |  | SIS |  | CM_V2W
XIS_89554 |  | SIS |  | CM_V2W
XIS_39441 |  | SIS |  | CM_V2W
XIS_39741 |  | SIS |  | CM_V2W
XIS_30027 |  | SIS |  | CM_V2W
XIS_90001 |  | SIS |  | CM_V2W
XIS_91001 |  | SIS |  | CM_V2W
XIS_91201 |  | SIS |  | CM_V2W
XIS_91501 |  | SIS |  | CM_V2W
XIS_91506 |  | SIS |  | CM_V2W
XIS_91601 |  | SIS |  | CM_V2W