TAG | CM_VDB_V3:AOI | OUT_Dribble | Dribble Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Closed | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Open | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Dribble | Dribble Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OutHealth_Dribble | Dribble Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Dribble | Valve In Dribble Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | locManDribble |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | onsToDribble |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | locDribbleFromOpen |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD2S_MOR_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_Running |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_AtRef |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_LO |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_HI |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_Run |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InHealth_Running |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InHealth_AtRef |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_LO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_HI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD525Ctrl_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_VFD |  | AB:PowerFlex525V_E_ABF89C61:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_VFD |  | AB:PowerFlex525V_EENET_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD755_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_VFD |  | AB:PowerFlex755_E_3F9B8FFE:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OUT_VFD |  | AB:PowerFlex755_EENET_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDANA_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | LevelIndicator |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OUT_Ref |  | INT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | InHealth_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OutHealth_Scaled |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ConditionedOut |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDCH_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | IN_Status |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | OUT_Command |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | RunForward |  | OUT_Command.0
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | RunReverse |  | OUT_Command.1
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | Reset Drive Fault |  | OUT_Command.3
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | NetControl |  | OUT_Command.5
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | NetReference |  | OUT_Command.6
TAG | CM_VFDCH_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | CommStatus |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | InHealth_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | DriveMSG | Drive Communication | MESSAGE |  | (Usage := InOut, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | tmrMSGInterval | Data Via Message Interval Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | MsgState | Message State Engine | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CIPMessage | CIP Message Configs | SM_CIPMsg_V1[5] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CIPConfig | CIP Read Drive Configs | SM_CIPMsg_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CFGState | Config Message State | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | DINStatus | Digital In Status Of Drive | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
COMMENT | CM_VFDCH_V3:AOI | DINStatus | HOA In Auto |  | DINStatus.0
COMMENT | CM_VFDCH_V3:AOI | DINStatus | Drive Enabled |  | DINStatus.1
TAG | CM_VFDCH_V3:AOI | VFDFaultCode | VFD Fault Code - Read Only If Fault Exists | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ReqRunHold | Request Run Hold Register | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsMsgErr | Message Error ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | RawSpeedActual |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | DriveState | 1=Startup, 2=NotReady, 3=Ready, 4=Enabled, 5=Stopping, 6=FaultStop, 7=Faulted | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | RefCmd | Scale Commanded Reference | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ParamMSGFailed | Drive Reference Parameter Error | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsProcessReadData |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsResult |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsReadConfig |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsHOA_OFF |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF700_V1:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_VFD |  | AB:PowerFlex700VC_DE65F68A:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OUT_VFD |  | AB:PowerFlex700VC_C4120625:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF700_V2:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_VFD |  | AB:PowerFlex700VC_DE65F68A:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OUT_VFD |  | AB:PowerFlex700VC_C4120625:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF70_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_VFD |  | AB:PowerFlex70_EB4AE803:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OUT_VFD |  | AB:PowerFlex70_A9D06D0C:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF753_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_VFD |  | AB:PowerFlex753_R_3F9B8FFE:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OUT_VFD |  | AB:PowerFlex753_ENETR_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Start | Start Drive Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Stop | Stop Drive Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Disconnect | Disconnect Switch Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Running | Running Forward or Reverse | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_ReqREV | Request Reverse Operation | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Warning | Drive Warning | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Ready | Drive Ready | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_NetCtrl | Controlled From Network | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_NetRef | Reference From Network | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_AtRef | At Reference Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Accel | Accelerating | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Decel | Decelerating | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | OUT_Ref |  | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | CommStatus |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | InHealth_Inputs | Start Drive Input Health Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | InHealth_Outputs | Manual Mode Request Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | OUT_Reference | Output Reference (0-100%) | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_VFD_V3:AOI | IN_FailToRunDelay |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_VFD_V3:AOI | AutoCMDMan | Auto Command In Manual Monitor | SM_AutoCMDMan_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | SpeedValidate | Speed Validation Holding Register | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrRunTime | Total Run Time Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrFailedToRun | Failed To Run Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrResetVFD | Reset Hold To VFD | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseRef |  | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseBy1 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseBy0 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FltLockOut | Fault Lock Out Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | dintWrkgRunHrs | Working Amount of Run Time Hours | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | PrevInUseBy1 | Previous In Use By Result 1 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | PrevInUseBy0 | Previous In Use By Result 0 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | MsgParamVal | Returned Parameter From internal Message | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ModuleStatus | Fault/Warning Status (>0=Fault;<0=Warn) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FltActive | Status Of All Active Faults/Warnings | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CMDAutoDINT | Number of DINTs Used In Auto Command | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CMDAutoSizeMan | Offset Size Of The Auto Array When In Manual | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsMsgType | Message ONS | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | RefCmd | Commanded Reference | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | NotFaultedONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | bAutoCmdInMan | Auto Command In Manual Received | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | bInUse | Being Used Or In Manual | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsAutoRunRequest | Auto Run Request Is Issued ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsNotInUseSpeed | Not In Use ONS for Speed Ref | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsZoneFltReset | Zone Fault Reset ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsProdZoneFltReset | ONS Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ProdZoneFltReset | Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ExternalFault | External Fault Is Active | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ExternalBit | External Fault Bit Including Offset | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | RateSetpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KPStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KIStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KDStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrMaxRunTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VPRANA_V3:AOI | UDT |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_CloseLS | Close Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | CM_VPRANA_V3:AOI | IN_OpenLS | Open Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | CM_VPRANA_V3:AOI | IN_AnalogLS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OUT_Solenoid | Energize Block Solenoid | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OUT_CV | Output Control Variable | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_Status | Analog Channel Status | SINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | InHealth_CloseLS | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | InHealth_OpenLS | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OutHealth_CV | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | SetLSClosed | Set Closed Limit Switch Value When Using Analog Feedback | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Open |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_NormalOpen | Normal Divert Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | RateSetpoint | Rate Setpoint$NTo Ramp Controller | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | PrevRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | PrevRampRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | CalRampRate | Calculated Ramp$NRate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | ActiveRampingSetpoint | Ramping Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KPStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KIStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KDStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | locTaskRate |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VPR_V3:AOI | UDT |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_CloseLS | Close Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_OpenLS | Open Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OUT_Solenoid | Energize Block Solenoid | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OUT_CV | Output Control Variable | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_Status | Analog Channel Status | SINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | InHealth_CloseLS | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | InHealth_OpenLS | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OutHealth_CV | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Open |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_NormalOpen | Normal Divert Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_AnalogInput | HART Analog Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_Travel | HART Travel Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_SupplyPrs | HART Input Supply Pressure | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_DriveSignal | HART Drive Signal | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | RateSetpoint | Rate Setpoint$NTo Ramp Controller | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PrevRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PrevRampRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | CalRampRate | Calculated Ramp$NRate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ActiveRampingSetpoint | Ramping Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KPStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KIStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KDStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | locTaskRate |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrDriveSignalHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | DriveSignalHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | DriveSignalLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrDriveSignalLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrAnalogInputHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AnalogInputHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrAnalogInputLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AnalogInputLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrSupplyPrsHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | SupplyPrsHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrSupplyPrsLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | SupplyPrsLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrTravelHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | TravelHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrTravelLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | TravelLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrPositionFlt |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PositionFltPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ValvePosDiff | Valve Position Difference | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | HartVlvFlt |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VSL_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_CloseCMD | Close Command From Master | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OpenCMD | Open Command From Master | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_ModeCMD | Automatic Mode Command | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_ClosedLS | Limit Switch Closed Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OpenedLS | Limit Switch Open Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_CLSHealth | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OPNHealth | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_Out1Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_Out2Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locAutoInUse |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WSGE_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | BaseResolution |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Invert |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit4 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit8 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit10 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit20 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit40 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit80 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit100 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit200 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit400 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit800 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit1000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit2000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit4000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit8000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit10000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit20000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit40000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit80000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Sign |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | InHealth | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | ScaleReal | Scale Value | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDIn | Input BCD as DINT | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDConditioned |  | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | uWeight | Unsigned Weight From BCD | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | RawWeight | Signed Weight | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDValid |  | SM_BCDMonitor_V1[5] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | EnableCustom0 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WSP_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | IN_RawWeight | Raw Weight$Nfrom the Weigh Scale | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_WSP_V3:AOI | InHealth_Comm |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | IntOffset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WS_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | IN_RawWeight | Raw Weight$Nfrom the Weigh Scale | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | InHealth_RawWeight | Input Health of I/O Point | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | IN_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_WS_V3:AOI | IN_DLYType |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_WS_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsNotRunning | Not Running ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoLoss | Auto Loss ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoGain | Auto Gain ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsNumofCycles | Number of Cycles One Shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bAutoCmdInMan | Auto Command In Manual Received | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bInUseLoss | Being Used Or In Manual Loss | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bInUseGain | Being Used Or In Manual Gain | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | CM_WS_V3:AOI | SimInit | Simulation Initialize Values | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoStab | Auto Stabilize ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsSettle | Settling ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsProdZoneFltReset | ONS Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ProdZoneFltReset | Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsZoneFltReset | Zone Fault Reset ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsInitMeterTotal |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | HI | High Limit Exceeded | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LO | Low Limit Exceeded | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | NotFaultedONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsTolerance | Tolerance Evaluation ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LossBy1 | Loss By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LossBy0 | Loss By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | GainBy1 | Gain By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | GainBy0 | Gain By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | PrevInUseBy1 | Previous In Use By Result 1 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | PrevInUseBy0 | Previous In Use By Result 0 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | nFlowRatePreviousTime | Flow Rate Calculation Time at the last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | nFlowRateDeltaTime | Flow Rate Calculation Time Accumulated Since the Last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FltActive | Status Of All Active Faults/Warnings | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoDINT | Number of DINTs Used In Auto Command | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoZeroSize | Size of The Auto Zero Registers | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoSizeMan | Offset Size Of The Auto Array When In Manual | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | SimWeight | Simulation Weight Value (Used in Sim Mode Only) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rFlowRatePeriodWeight |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rWeightPerScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rCapturedTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rTotalSinceInit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rInitMeterTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rTotalPreviousScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | StoredWeight |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoRef |  | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCMD | OR Values For AutoOpen and AutoClose | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FltLockOut | Fault Lock Out Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrSim |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | StableTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrLowFlow | Low Flow Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrFlowRateAcc | Timer used to calculate the flow rate | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrLoFaultDelay | LO Fault Delay Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrHiFaultDelay | HI Fault Delay Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCMDMan |  | SM_AutoCMDMan_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExternalFault | External Fault Is Triggered | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateCTL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateCTL2 |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateAve_Unload |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateArray |  | REAL[20] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | flowenable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsflowenable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rWeightPerScanTest |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | ConvertToElapsedTime:AOI | Input_Timer |  | TIMER |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | ConvertToElapsedTime:AOI | Output_ElapsedTime |  | TIME_ELAPSED |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | ConvertToElapsedTime:AOI | CountDown |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | ConvertToElapsedTime:AOI | Secs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Hrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Mins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | RemainingSecsFromHrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | RemainingSecsFromMins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Secs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Hrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_RemSecsFromHrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Mins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_RemSecsFromMins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Mins_Reduced |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | SET_MIN_Scaled |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | SET_SECS_Scaled |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | TimeValueMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | AccumMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | PresetMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_ADDPOT_V1:AOI | UDT |  | uEM_ADDPOT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | TopInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | BotInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_AGIT_M2S_V3:AOI | UDT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | Motor |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | MixTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCycleAgitationOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCycleAgitationOn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevInLowSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevInHighSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Agitator_Reference_Val |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ModeChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Inst_ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedMixTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedCycleOffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedCycleOnTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrMaxAgitTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | onsMaxAgitTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | onsMaxAgitFLT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAgitHeldInCycle |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrMaxAgitTimeInAgitation |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_AGIT_VFD_V3:AOI | UDT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | Motor |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | MixTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCycleAgitationOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCycleAgitationOn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevInLowSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevInHighSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Agitator_Reference_Val |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ModeChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedMixTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedCycleOffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedCycleOnTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrMaxAgitTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | onsMaxAgitTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ShutoffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | onsMaxAgitFLT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAgitHeldInCycle |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrMaxAgitTimeInAgitation |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CoFeed_V2W_V2W_V3:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryA |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryA_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryB |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryB_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | Cofeed_AOI |  | AA_CoFeed_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CoFeed_V2W_V2W_V4:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryA |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryA_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryB |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryB_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | Cofeed_AOI |  | AA_CoFeed_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CONT_DLY_V1:AOI | UDT |  | uEM_CONT_DLY_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | Scale |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ContIndex | Used to Search For Matching Container | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RMIndex | Raw Material Index Used For Finding Raw Material in a Container | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_Cont |  | udsContTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTContIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_RM |  | udsMatTracking[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ScaleIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_Tare |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ReweighActive |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ContAmt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Container_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Container_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RM_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RM_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Cont_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Cont_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTCont_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTCont_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RW_Source | Rework Source Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Water_Source |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Source | Washwater Delivery Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | NonGPWW_Source | Non Generic Paint Washwater Source | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | MaxGPToAllowWater | Maximum GP Percentage before$Nswitching to Virgin Water is NOT allowed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | EnableWWFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Delivery_Done |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Delivery_Active |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SetpointRef |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SetpointChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DGP_V2W_AOD_R_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RW_Source | Rework Source Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Water_Source |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Source | Washwater Delivery Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | NonGPWW_Source | Non Generic Paint Washwater Source | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | MaxGPToAllowWater | Maximum GP Percentage before$Nswitching to Virgin Water is NOT allowed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | EnableWWFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Delivery_Done |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Delivery_Active |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SetpointRef |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SetpointChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_PREWEIGH_V1:AOI | UDT |  | uEM_DLY_PREWEIGH_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_Status |  | uEM_STATUS_V1[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | stsIndex |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DLY_PREWEIGH_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_STATUS_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_STATUS_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | MatchLotNumb |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_SCALE_V1:AOI | UDT |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | valContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Scale_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Scale_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_EarlyComplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ActiveFinal_Test |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DeliveryDiff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ActualLastScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_SCALE_V2:AOI | UDT |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | valContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Scale_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Scale_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_EarlyComplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ActiveFinal_Test |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DeliveryDiff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ActualLastScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | PurgeValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | tmrAirPurge |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourcePump |  | uCM_DPH_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_DPH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourcePump |  | uCM_DPH_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_PMR_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourcePump |  | uCM_PMR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | tmrMeterPumpIn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | MeterPumpInACC |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V3W_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | TankInletValve |  | uCM_V3W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V3W_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | TankInletValve |  | uCM_V3W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | WaterValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | InitialAmountToStartPump |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | PumpDelayOffSec |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrPumpDelayOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | STS_FillingTube |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrFillingTube |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_HOLD_V1:AOI | UDT |  | uEM_HOLD_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | ExternalReset | External Timer Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | ExternalHold | External Timer Hold | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | HoldTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_INERT_V2W_V1:AOI | UDT |  | uEM_INERT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | SourceValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | BlanketValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | BypassValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | InertFlowRate | Inert Gas Flow Rate | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | VesselPrs |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | UDT_DLY |  | AA_INERT_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | Deadband_Cooling |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | Deadband_Heating |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | HighDeadband |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | LowDeadband |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | PrsDebounce |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PMPT_V1:AOI | UDT |  | uEM_PMPT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | zzzdelete |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | VentValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | BypassValve | Bypass Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR1 | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDT_PRS |  | AA_PRS_Extension_Blanket_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_RCH_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VentValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPumpInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | PressureVentHDR | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacHDR | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | CoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | CoolWaterOutletTemp | Primary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPumpInletPrs | Vac Pump Inlet Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | LocalStartPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | LocalStopPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | WaterInletValve | Pump Water Inlet Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | UDT_PRS |  | AA_PRS_RCH_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacBypassValve | Secondary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacPump | Secondary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | ScrubPumpRng | Scrubber Pump Running Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PressureVentHDR | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacHDR | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacHDR | Secondary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterInletTemp | Primary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterOutletTemp | Primary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimDemisterLS | Primary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterFlow | Secondary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterInletTemp | Secondary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterOutletTemp | Secondary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecDemisterLS | Secondary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimHOA_InAuto_FS | Primary HOA Switch In Auto | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimHOA_InHand_FS | Primary HOA Switch In Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecHOA_InAuto_FS | Secondary HOA Switch in Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecHOA_InHand_FS | Secondary HOA Switch In Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | Open_FS | Open Field Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | UDT_PRS |  | AA_PRS_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_QC_V1:AOI | UDT |  | uEM_QC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_QD_V2W_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | OutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | DischargeValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Quadro |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | OperLight |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | QUADRO_PB | Pushbutton at the $NQuadro Station | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | FlushTarget |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | ONSFlushTarget1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | ONSFlushTarget2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Flash_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Flash |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | tmrMaxFlushTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | QuadroFlushing |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Internal_OperLight |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | FlushComplete |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_AOD_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_M2S_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_VFD_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RSC_MGR_V3:AOI | IN_USE | Resource is in use by some equipment | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | IN_QUEUE | Resource Request Exists for this Equipment | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | UDT |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | Devices |  | EM_RSC_MGR_DEVICE_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | ProdLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | CFG_MAX_ID | MAXIMUM ID NUMBER | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_CNTR_1 | Counter to Check if Request Already in queue | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_REQUEST_QUEUE |  | DINT[100] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_POS_OF_REQ_IN_QUEUE |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FIFO_CONTROL | LOAD AND UNLOAD QUEUE | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FFU_DEST | Unload Destination for FIFO | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_REQUEST_QUEUE_BUFFER |  | DINT[100] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_CONTROL_1 | LOAD SEARCH | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_STEP_1 | LOAD | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_Ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.0
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.1
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.2
TAG | EM_RSC_MGR_V3:AOI | WRK_SEQ_BIT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_CONTROL_2 | UNLOAD SEARCH | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_STEP_2 | CLEAR | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FAL_CONTROL_1 | CLEAR$NQUEUE | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_2_COPY_LENGTH |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_COPY_FROM_POS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_BIT |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
COMMENT | EM_RSC_MGR_V3:AOI | WRK_BIT | BANG BIT |  | WRK_BIT.0
TAG | EM_RSC_MGR_V3:AOI | CFG_MAX_QUEUE | MAXIMUM NUMBER IN QUEUE | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | StateNumberRef | State Ref to determine if state has Changed | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | StateChange | State Had Changed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | REST_DEVICE |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | REST_CONTROL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | RESET_DEVICES |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | PathTime | Minimum Time $Nthe Current Path$Nmust be maintained $Nbefore moving to next Path | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | OUT_DEVICES_DINT_FM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | OUT_DEVICES_DINT |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Index |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | IN_DEVICES_DINT |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | HOLD_DEVICES |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | FaultTime | MaxiumumTime $Nthe Current Path$Nmay be executed$Nbefore moving to next Path | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | DeviceOutput_PathMet |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | CMP_CONTROL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Test_Pos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | BLANK_Mask |  | EM_RSC_MGR_DEVICES_LIST_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | LastUsedInstruction |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | PathSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SourceIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | LoopIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | EnableSearch |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SearchSource |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | clearindex |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SearchItem |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SourceDone |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | DelaytoDisable |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | CurrentUserRef |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SubQueueSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QueueUserID |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QLoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QResetONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringDestinationPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringTankNumber |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locLengthDifference |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringAltPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStartPos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringSourceIndex |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringSource |  | STRING |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_STATUS_V1:AOI | UDT |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_BottomValveClosed | Tank Bottom Valve Closed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_Weight |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_Temp |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | PreventNewOrder | Prevent New Order From Loading | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | BypassDropBit | Bypass The Internal Drop Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_Cont_DLY |  | uEM_CONT_DLY_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_DLY_Scale |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_DischPrs |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | SourceProps |  | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | SourceInfo |  | SM_SourceInfoTable_V2[40] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | DestinationLevel |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | BLANK_STRING82 |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Major |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Minor |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Ext |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExtReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | FP |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | UDTVer |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DLYIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Status | Bits$N0=Not Active Was Not Active$N1=Active, Reset When Complete | BOOL[416] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | OneSec |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_VAL_Active |  | REAL[385] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_VAL_ActiveTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | SourceTankInst |  | SM_SourceTankValidate_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DLYIndex1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ContDlyCompleteONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ONS | One-Shots | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | XferIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DlyScaleCompleteONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | UseDLYForStartTimer |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | MessageResetDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPJK_V1:AOI | UDT |  | uEM_TEMPJK_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SteamInlet | Steam Supply$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | WaterPump | Water Supply Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRM |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV1 | Safe State Valve 1 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV2 | Safe State Valve 2 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV3 | Safe State Valve 3 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV4 | Safe State Valve 4 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV5 | Safe State Valve 5 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV6 | Safe State Valve 6 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV7 | Safe State Valve 7 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV8 | Safe State Valve 8 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV1 | Safe State Valve Off 1 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV2 | Safe State Valve Off 2 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV3 | Safe State Valve Off 3 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV4 | Safe State Valve Off 4 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV5 | Safe State Valve Off 5 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV6 | Safe State Valve Off 6 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | UDT_TEMPJK |  | AA_TEMPJK_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locSafeState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | UDT_TEMPC |  | AA_TEMPVC_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_V2:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | UDT_TEMPC |  | AA_TEMPVC_V2 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_VFD_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Pump | Inlet Pump | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | UDT_TEMPVC |  | AA_TEMPVC_VFD_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PumpVFD |  | uCM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_VENT_V2W_V1:AOI | UDT |  | uEM_VENT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | SourceValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ScrubValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | BypassValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | UDT_VENT |  | AA_VENT_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EP_Ctrl_V2:AOI | UDT |  | uEP_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EP_Ctrl_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EP_Ctrl_V2:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | Minor |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | Major |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | FP |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EX_REQ_V3:AOI | UDT |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1Confirmed | HDR1 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2Confirmed | HDR2 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3Confirmed | HDR3 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | OutletValveConfirmed | Outlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | InletValveConfirmed | Inlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | PumpConfirmed | Pump is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2PrevState | Header 2$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2Ready | Header 2$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3PrevState | Header 3$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3Ready | Header 3 $NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1PrevState | Header 1$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1Ready | Header 1$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | tmrFaultReset |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | onsZoneFltReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FltActive |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FltLockOut |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FaultCodeHolding |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | ModuleStatus |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | onsCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibAnalog_Input:AOI | Alarm_Ack | All Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_Disable_Req | Disable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Alarm_Enable | Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_Enable_Req | Enable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Alarm_HI | HI Level Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_HIHI | HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_LO | LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_LOLO | LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | FAULT | Analog Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | FAULT_STS | Analog Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Analog_IN | Scaled Input from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Analog_Val | HMI Display Value | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Level_HI_Stpt | Level for HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_HIHI_Stpt | Level for HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LO_Stpt | Level for LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LOLO_Stpt | Level for LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libFM:AOI | Alarm_Ack | All Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Enable | Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Enable_Req | Enable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Alarm_Disable_Req | Disable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Alarm_HI | HI Level Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_HIHI | HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_LO | LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_LOLO | LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Totalizer | Totalizer Not Totalizing Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | FAULT | Meter Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | FAULT_STS | Meter Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Reset | Meter Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Total_Enbl | Totalizer is Installed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Was_Reset | Meter Was Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Status_Word_1 | Flow Meter Status Word #1 | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | libFM:AOI | Status_Word_2 | Flow Meter Status Word #2 | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | libFM:AOI | Analog_IN | Scaled Input from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density | Density Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Drive_Gain | Drive Gain Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Level_HIHI_Stpt | Level for HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_HI_Stpt | Level for HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LO_Stpt | Level for LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LOLO_Stpt | Level for LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temperature | Temperature Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Total_IN | Totalizer from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Totalizer | Totalizer Display Value | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Rate | Flow Rate | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Zero_SP | Zero Limit Value SP | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_HI_Stpt | Density Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_HIHI_Stpt | Density Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_LO_Stpt | Density Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_LOLO_Stpt | Density Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_HI | Density Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_HIHI | Density HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_LO | Density LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_LOLO | Density LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_HI | Temperature Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_HIHI | Temperature HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_LO | Temperature LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_LOLO | Temperature LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_HI_Stpt | Temperature Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_HIHI_Stpt | Temperature Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_LO_Stpt | Temperature Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_LOLO_Stpt | Temperature Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_HI | Drive Gain Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_HIHI | Drive Gain HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_LO | Drive Gain LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_LOLO | Drive Gain LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_HI_Stpt | Drive Gain Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_HIHI_Stpt | Drive Gain Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_LO_Stpt | Drive Gain Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_LOLO_Stpt | Drive Gain Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Alm_Total_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Total_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Total_Storage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libHOA:AOI | IN_AUTO | HOA In Auto | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | IN_HAND | HOA In Hand | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | IN_OFF | HOA In Off | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_AUTO | HOA Auto Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_HAND | HOA Hand Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_Pos_Flt | HOA Not In Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | MODE | HOA Mode$N1 = Hand and Auto$N2 = Hand Only$N3 = Auto Only | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibLvl_Switch:AOI | Alarm_Ack | All Level Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Alarm_Disable_Req | Disable Level Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Alarm_Enable_Req | Enable Level Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Alarm_HLS | High Level Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Alarm_LLS | Low Level Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | FAULT_STS | Device Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | FAULT | Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | HLS_Alarm_Enable | High Level Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LLS_Alarm_Enable | Low Level Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSH_INPUT | Level Switch High Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSL_INPUT | Level Switch Low Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSH_STS | Level Switch High Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | LSL_STS | Level Switch Low Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Level_HLS_Delay_Setpoint | High Level Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Level_LLS_Delay_Setpoint | Low Level Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Level_HLS_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | LibLvl_Switch:AOI | Level_LLS_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libMtr_Simulation:AOI | Create_Running_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libMtr_Simulation:AOI | Energize_IN |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libMtr_Simulation:AOI | Running_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libMtr_Simulation:AOI | RunTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libPump_Mtr:AOI | ALARM_ACK | Clear Device Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | AUTO_ACTIVATE | Auto Activation of Pump If Pump Is In Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | DISC_OK | Motor Disconnect Okay | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ENERGIZE | Pump Coil Energize to Field Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | FAULT | Pump Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FAULT_STS | Pump Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | FIELD_ACTIVATE | Field Activation Of Pump If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FlowReset | Reset Flow Total | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | HMI_Field | HMI Field Selected | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | INTERLOCK | Prevent the Motor from operating$N(1 = OK) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_BYPASS | Interlock Bypass$N(0 = No 1 = Yes $NOnly Functional if Bypassable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_BYPASSABLE | Allow Interlock Bypassing$N(0 = No 1 = Yes) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_ENABLED | Interlock Is OK Has Been Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_OK | Device Interlocks OK | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_RESET | Interlock Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | INTLK_RST_RQRD | Interlock Reset Required | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | LIMIT_OVR | Input Limit Switch Override | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | MAN_ACTIVATE | Manual Activation Of Pump If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | MAN_CMD_STS | Set from HMI Auto = 0 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | OFFDLYDSBLE | Off Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | OFF_ONS | Off One-Shot | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | OFF_STS | Pump is Off | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Pump | Device is a Pump | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUN_ONS | Run One-Shot | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | RUNDLYDSBLE | Run Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNNING_LIMT | Pump Running Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNNING_STS | Pump is Running | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalFlowAlarm | Motor Flow is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeAlarm | Motor Hours is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeReset | Cumulative Run Time Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TRANSITION | Pump Is Starting or Running Limit not On | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | VFD_Fault | VFD Faulted | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | VFD_RESET | VFD Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ACTVT_OUT1 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ACTVT_OUT2 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FaultCode | Fault Code From Drive | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Intlk_Dly | Interlock Delay Time | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_TYPE | Interlock Type$N( 0 = Force Stop 1 = Force Start) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | ModeType | 0=Auto & Manual Mode$N1=Auto Mode$N2=Manual Mode | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | OFFPreset | Off Time Preset | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNPreset | Run Time Preset | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | TotalFlowSP | Cumulative Flow Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalHrSP | Cumulative Run Time Hours Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Current | Motor Current | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FlowTotal | Total Flow | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_1 | Flow Meter Input #1 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_2 | Flow Meter Input #2 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_3 | Flow Meter Input #3 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_4 | Flow Meter Input #4 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_5 | Flow Meter Input #5 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Pressure | Motor Pressure | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Spd_Cmd | Speed Command | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Spd_Max | Maximum Motor Speed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Spd_Min | Minimum Motor Speed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Spd_Output | Speed Output | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Temperature | Motor Temperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeHrs | Cumulative Run Time Hours | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | PERMISSIVE_OK | Permissive To Operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Field_Start_PB | Field Start Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Field_Stop_PB | Field Stop Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | OFF_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | RUN_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | AUTO_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | CurrentHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | TemperatureHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | CurrentHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | TemperatureHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | PressureHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalTimer | Cumulative Run Time 1 Hour Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalHrsStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureLoFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureLoLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureDly |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | LoPrsEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalAddedCur | Total Current Amount Added | REAL[6] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | FlowONS | ONE-SHOT | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Meter_Prev |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalAddedPrev |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Meter_Mont |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | FlowStore |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiPrsEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiCurrentEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiTempEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Intlk_Dly_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | VFD_RESET_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | VFD_RESET_SP | VFD Reset On Time SP | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | RunDlyOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibSwitch:AOI | Alarm_Ack | All Switch Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | Alarm | Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibSwitch:AOI | FAULT_STS | Device Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | FAULT | Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | Alarm_Enable | Switch Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | INPUT | Switch Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | STS | Switch Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | Delay_Setpoint | Switch Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibSwitch:AOI | Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libValve_ACT_SOL:AOI | ALARM_ACK | Clear Device Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | AUTO_ACTIVATE | Auto Activation of Valve If Valve Is In Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_FLT | Valve Closed Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_ONS | Close ONS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_STS | Valve in the Closed Postion | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSED_LIMT | Closed Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CLSDLYDSBLE | Close Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CycleReset | Cycle Count Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CycleCntAlarm | Cycle Count Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ENERGIZE | Valve Coil Energize to Field Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | FAULT | Valve Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FAULT_STS | Valve Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | FIELD_ACTIVATE | Field Activation Of Device If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FlowReset | Reset Flow Total | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | INTERLOCK | Interlocks required for the device to operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_BYPASS | Interlock Bypass$N(0 = No 1 = Yes $NOnly Functional if Bypassable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_BYPASSABLE | Allow Interlock Bypassing$N(0 = No 1 = Yes) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_ENABLED | Interlock Is OK Has Been Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_OK | Device Interlocks OK | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_RESET | Interlock Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | INTLK_RST_RQRD | Interlock Reset Required | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | HMI_Field | HMI Field Selected | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | LIMIT_OVR | Limit Switch Override | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | MAN_ACTIVATE | Manual Activation Of Valve If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | MAN_CMD_STS | Auto/Man Device Status 1=Man | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_FLT | Valve Opened Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_LIMT | Open Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_ONS | Open ONS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | OPEN_STS | Valve in the Open Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | OPNDLYDSBLE | Open Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | SolPump | Device is a Pump | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | TotalFlowAlarm | Motor Flow is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeAlarm | Pump Hours is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeReset | Cumulative Run Time Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TRANSITION | Valve Is Moving Or Not At The Final Position | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ACTVT_OUT1 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number Bits 0-31 | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ACTVT_OUT2 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number Bits 32-63 | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ClosePreset | Amount of Seconds for Valve to Close | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CountSP | Cumulative Cycle Count Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CycleCount | Cumulative Cycle Counter | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | DeviceType | 0=No Limit 1=Closed Limit 2=Opened & Closed Limits | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | Intlk_Dly | Interlock Delay Time | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_TYPE | Interlock Type$N( 0 = Force Close 1 = Force Open) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | ModeType | 0=Auto & Manual Mode 1=Auto Mode$N2=Manual Mode | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | OpenPreset | Amount of Seconds for Valve to Open | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | TotalFlowSP | Cumulative Flow Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalHrSP | Cumulative Run Time Hours Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FlowTotal | Total Flow | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Meter_IN | Flow Meter Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeHrs | Cumulative Run Time Hours | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | PERMISSIVE_OK | Permissive To Operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Field_Open_PB | Field Open Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Field_Close_PB | Field Close Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_TMR | Closing Timer | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | OPEN_TMR | Opening Timer | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | AUTO_ONS | Auto ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | CYCLE_ONS | Cycle One-shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | FlowONS | ONE-SHOT | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalAddedCur | Total Current Amount Added | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | FlowStore |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalAddedPrev |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Meter_Mont |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Meter_Prev |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalTimer | Cumulative Run Time 1 Hour Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalHrsStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Intlk_Dly_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | CloseDly |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libValve_Simulation:AOI | Close_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | Create_Close_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_Simulation:AOI | Create_Open_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_Simulation:AOI | Energize_IN |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | Open_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | CloseTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_Simulation:AOI | OpenTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | MM_CIR_V1:AOI | UDT |  | uMM_CIR_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IndirectUserID | Indirect Using In Use By Registers | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IndirectUserType | Indirect Using In Use By Type Registers | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseA | Raw PhaseA Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseB | Raw PhaseB Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseC | Raw PhaseC Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | InHealth_Current | Input Health Current Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | STS_Enabled | MM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_Faulted | MM Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_SIM | Simulation Mode Is Active | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_SuppressAlarms |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | IN_SuppressAlarms |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | MM_CIR_V1:AOI | IN_DisableIndirectUse | Disable The IndirectUsing Instruction | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | MM_CIR_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locOffTooLong |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locWaitInRangeTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locIndirectUserID |  | DINT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locWaitMinOnTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locIndirectUsingAOI |  | SM_IndirectUsing_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | onsMaxTimeOFF |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | onsAutoResetSFTimeOff |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Receive_AIN_V1:AOI | UDT_AIN |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | EX_REQ |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | pc_IN_AIN |  | PC_Remote_CM_AIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | pc_OUT_AIN |  | PC_Remote_CM_AIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | PC_ConnStat | Produced/Consumed Connection Status 1=Good | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | COMMS_OK |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | ACTIVE |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_AIN_V1:AOI | AOI_EX_REQ |  | EX_REQ_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Receive_AIN_V1:AOI | loc_InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_AIN_V1:AOI | loc_MaxInUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_AIN_V1:AOI | loc_InUseWritePos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_AIN_V1:AOI | loc_NoInUseOverrun |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Receive_DIN_V1:AOI | UDT_DIN |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | EX_REQ |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | pc_IN_DIN |  | PC_Remote_CM_DIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | pc_OUT_DIN |  | PC_Remote_CM_DIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | PC_ConnStat | Produced/Consumed Connection Status 1=Good | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | COMMS_OK |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | ACTIVE |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_DIN_V1:AOI | AOI_EX_REQ |  | EX_REQ_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DIN_V1:AOI | loc_InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DIN_V1:AOI | loc_MaxInUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DIN_V1:AOI | loc_InUseWritePos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DIN_V1:AOI | loc_NoInUseOverrun |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Receive_DOUT_V1:AOI | UDT_DOUT |  | uCM_DOUT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | EX_REQ |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | pc_IN_DOUT |  | PC_Remote_CM_DOUT |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | pc_OUT_DOUT |  | PC_Remote_CM_DOUT |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | PC_ConnStat | Produced/Consumed Connection Status 1=Good | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | COMMS_OK |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | ACTIVE |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_DOUT_V1:AOI | AOI_EX_REQ |  | EX_REQ_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DOUT_V1:AOI | loc_InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DOUT_V1:AOI | loc_MaxInUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DOUT_V1:AOI | loc_InUseWritePos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_DOUT_V1:AOI | loc_NoInUseOverrun |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Receive_V2W_V1:AOI | UDT_V2W |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | EX_REQ |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | pc_IN_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | pc_OUT_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | PC_ConnStat | Produced/Consumed Connection Status 1=Good | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | COMMS_OK |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | ACTIVE |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | AOI_EX_REQ |  | EX_REQ_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_MaxInUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_InUseWritePos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_NoInUseOverrun |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Send_AIN_V1:AOI | UDT_AIN |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | pc_IN_AIN |  | PC_Remote_CM_AIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | pc_OUT_AIN |  | PC_Remote_CM_AIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | PC_ConnStat | Produced/Consumed$NConnection Status | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_AIN_V1:AOI | CM_UDT_AIN |  | CM_AIN_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_AIN_V1:AOI | SM_RequestUse_AutoEnable |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_AIN_V1:AOI | loc_InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Send_AIN_V1:AOI | loc_InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Send_DIN_V1:AOI | UDT_DIN |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | pc_IN_DIN |  | PC_Remote_CM_DIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | pc_OUT_DIN |  | PC_Remote_CM_DIN |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | PC_ConnStat | Produced/Consumed$NConnection Status | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DIN_V1:AOI | CM_UDT_DIN |  | CM_DI_V5 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_DIN_V1:AOI | SM_RequestUse_AutoEnable |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_DIN_V1:AOI | loc_InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Send_DIN_V1:AOI | loc_InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Send_DOUT_V1:AOI | UDT_DOUT |  | uCM_DOUT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | pc_IN_DOUT |  | PC_Remote_CM_DOUT |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | pc_OUT_DOUT |  | PC_Remote_CM_DOUT |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | PC_ConnStat | Produced/Consumed$NConnection Status | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_DOUT_V1:AOI | CM_UDT_DOUT |  | CM_DOUT_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_DOUT_V1:AOI | SM_RequestUse_AutoEnable |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_DOUT_V1:AOI | loc_InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Send_DOUT_V1:AOI | loc_InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Send_V2W_V1:AOI | UDT_V2W |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | pc_IN_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | pc_OUT_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | PC_ConnStat | Produced/Consumed$NConnection Status | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | CM_UDT_V2W |  | CM_V2W_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | SM_RequestUse_Open |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | SM_RequestUse_Close |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | loc_InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | loc_InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_AutoCMDMan_V1:AOI | IN_Auto |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_AutoCMDMan_V1:AOI | Secondary | Secondary CMD Input - (DINT[0] > 0) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Average:AOI | NumOfItems | Number to Points to Average | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Average:AOI | LOAD_AVG |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Average:AOI | Average_OUT |  | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Average:AOI | UNLOAD_AVG |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Average:AOI | Average_Array |  | REAL[20] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Average:AOI | Average_CTL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | SM_Average:AOI | Average_CTL_2 |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_BCDMonitor_V1:AOI | Bit0 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit3 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | BCDValue |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CC_V3:AOI | UDT |  | uSM_CC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CC_V3:AOI | tmrCMDRec |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CHAR_V1:AOI | Char |  | uSM_CHR |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CHAR_V1:AOI | HEADER_B | File Header Labels for CM Routines Bxx | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_PROC_HIGH_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_PROC_LOW_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_MULT_HIGH_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_MULT_LOW_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_ChaseWaterValve:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR1InService | Header 1 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR2InService | Header 2 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR3InService | Header 3 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR4InService | Header 4 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR5InService | Header 5 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR6InService | Header 6 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR1_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR2_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR3_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR4_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR5_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR6_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | ActiveHDRIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | priorityindex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | CountSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | CountMax |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | PrimaryHDRPriority |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | initalscancomplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | PreviousPriority |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | NoChaseActive | No Chase Is Currently Active$NOpen All Chase Valves | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_A |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_B |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_Dest |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Count_V1:AOI | IN_Pulse |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | OUT_Count |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | IN_Stopped | Accummulate Pulses When Not Stopped. Reset Counter When Stopped | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Count_V1:AOI | Counter |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Count_V1:AOI | IN_Pulse_ons |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_ExternalFaultResolve_V1:AOI | FaultWord |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | LastInternalFaultBit |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | FaultBitOutput |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | FaultBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ExternalFaultResolve_V1:AOI | ActiveFault |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_HoseConnect_V1:AOI | HoseConnect |  | uSM_HoseConnect_V1[10] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | UDT |  | uSM_HoseConnect_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SourcePath |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | AltPath |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | UserBitID |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SEQIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SEQ_FD |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | InputDevices |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | Mask |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | OutputDevices |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | locSEQSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSEQIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strSource |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strAltPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strSourcePath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locLoopIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSearchValue |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSEQPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locMask |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locStatus |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | OP1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | OP2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | L9_P1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | L9_P2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_OP1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_OP2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_L9_P1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_L9_P2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | IndexEqual |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_HosePreact:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | FlowrateThreshold | Flowrate is above this Threshold, Use System Preact. Othewise Use Hose Preact | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | TimeToClose | Inlet Valve Time to Close | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | FRFactor | Multipler to Flowrate Adjustment | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_HosePreact:AOI | HosePreact |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_HosePreact:AOI | CurrentFlowrate |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | SourceInfoPreact |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | onsCapturePreact |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | LowFlow |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | UseFixedPreact |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | PreactTemp |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | DisableIndirect | Disable Indirect Using | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | PrevInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | PrevInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_IndirectUsing_V3:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectUsing_V3:AOI | AutoEnable |  | DINT[17] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectUsing_V3:AOI | DisableIndirect | Disable Indirect Using | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_IndirectUsing_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | PrevInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | PrevInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Interlock_V1:AOI | IN_Interlock |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_Fout | Secondary CMD Input - (DINT[0] > 0) | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_IlkBypass |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | OUT_Sts_Interlocked |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Interlock_V1:AOI | CMD_ResetFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_FLT_Interlock |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | Not_Bypassed |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_InUseByUsing_V3:AOI | InUseByIndex | In Use By Array Index | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeID | Module Reference Type ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeIndex | Module Type Index | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeArrayRef | Module Array Ref | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyBitID |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyModuleStatus | Module Status Information | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UsingArray |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeID | Type ID Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeIndex | Type Index Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserPriority | Fast Track Priority Level (1=Highest) | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | ER | Error Status Bit | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | FL | Module Array Of Current User Is Full | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | DN | Done Status Bit | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeArrayRef | Type Array Reference Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | GlobalID | The Calculated Global ID | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousUsedBy | InUseBy Value of Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | FSC_Ctrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousGlobalID | Global ID From The Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousCount | Determine Count Previous Entry Count | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | CopyLen | Length Required To Move Data | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | Count | Count From InUseBy List | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | MaxUsing | Maximum Users Configured In System | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | MaxModules | Maximum Modules Allowed To Be Used | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | CopyStartPosition | Copy Array First Position | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | UserBitID | Bit ID Of Used Object (Not Applicable to CMs) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_MessageGroupMember_V1:AOI | EnableMSG | End Point Device Is In Use | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | TokenTag | Group Token Tag | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | MyID | My Group Token ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | NextID | Next Group Token ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | Message |  | MESSAGE |  | (Usage := InOut, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | MSGConfigs |  | SM_CIPMsg_V1[5] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | CurrentResultIndex | Index Of Current Result | INT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_MessageGroupMember_V1:AOI | STS_Processing |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | locMSGIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locProcessing |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locMSGSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locLastPass |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | onsDone |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | onsNext |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Preact:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Preact:AOI | PreactAdjMinAddThreshold | Minimum Addition Setpoint to Allow for Preact Adjustment$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | PreactFlowAdjEnable | Preact Flow Adjustment Enable/Disable$N(1 = Enable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | CalcPreactTimeAdj | Calculated Prect Time Adjustment | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | CalcPreactErrAdjust | Calculated Preact Error Adjustment$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | MaxPreactTime | Maximum Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinPreactTime | Minimum Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MaxPreact | Maximum Preact Setpoint$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinPreact | Minimum Preact Setpoint$N(Lbs) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | ErrPercent | Error Percent For Last Addition$N(%) | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | PreactAdjustPercent | Preact Adustment Percent Setpoint$N(%) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | PreactEnable | Enable/Disable Auto Preact Adjustment$N(1 = Enabled) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinFlowRateSP | Minimum Flow Rate for Preact Calculations | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | Index | Array Position | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Preact:AOI | CurrentFlowrate |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | onsCaptureError |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | FlowLbPerSecStore | Stored Flow Rate While System Running | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | AdditionErrorSample | Addition Error For Preact Adjustment Sample Number | REAL[4] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | UpdatePreactCalcs | Update Preact Calculation | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | AdditionAvgError | Addition Average Error for Preact Adjustment | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | PreactAdjustCmd | Preact Adjustment Command | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | PreactTimeSP | Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read Only)
TAG | SM_Preact:AOI | onsReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | MissCharge |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | EID |  | STRING_20 |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | SM_Preact:AOI | DESC |  | STRING_40 |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_RequestUse_V1:AOI | IN_AutoReq | Auto Request Array | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_RequestUse_V1:AOI | DelayEnableOut |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_SourceTankValidate_V3:AOI | SourceInfo |  | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceProp |  | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceMES | Source Tank from MES | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceInfoStorageIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourcePropIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourcePath | Source AltPath | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | TankPath | Destination AltPath | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | Storage_FD | Found In Source Info Storage | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SP_FD | Found In Source Properties | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | DN | Read Full Array | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | ListSize | Max Size Of Lookup List$N | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | LoopIndex | Loop Index Value | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SearchTank | Tank To Lookup$N | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SourcePropSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SourceInfoTable |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | DeliveryEMInfo |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SearchValue |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | locDeliveryEMInfoIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | locSourcePropIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | locSourceInfoStorageIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | strSource |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strAltPath |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strSourcePath |  | STRING_20 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strMyTankNumber |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strMyTankNumberPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_WEP_UnloadRangeCheck_V1:AOI | LI_As_AIN |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_WEP_UnloadRangeCheck_V1:AOI | LevelToUnload |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | Modules | C03_PURGE | ===========================================================================================================$NXIS_89101 Purge Control (Deprecated in favor of using the Prompting method)$N===================================================================== | (SM_CC_PURGE_XIS_89101,CC_PURGE_XIS_89101) | 0
RCOMMENT | Modules | C03_PURGE | ===========================================================================================================$NXIS_89501 Purge Control (Deprecated in favor of using the Prompting method)$N===================================================================== | (SM_CC_PURGE_XIS_89501,CC_PURGE_XIS_89501) | 5
RCOMMENT | Modules | C03_PURGE | ===========================================================================================================$NXIS_89601 Purge Control (Deprecated in favor of using the Prompting method)$N===================================================================== | (SM_CC_PURGE_XIS_89601,CC_PURGE_XIS_89601) | 10
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NTruck Unloading Station Prompt Generation Logic$N================================================================================================= | NOP() | 0
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT80000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T800.CMD.Reset) | 1
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT82000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T820.CMD.Reset) | 4
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT83000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T830.CMD.Reset) | 7
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT84000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T840.CMD.Reset) | 10
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT85000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T850.CMD.Reset) | 13
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT86000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T860.CMD.Reset) | 16
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT87000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T870.CMD.Reset) | 19
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NT88000 Prompting Commands. Initiated from Resource Manager.$N===================================================================================== | OTL(CC_PROMPT_STOP_SOURCEPUMP_T880.CMD.Reset) | 22
RCOMMENT | Modules | C04_PROMPTING | ===========================================================================================================$NCustom Command Rungs$N=========================================================================================================== | (SM_CC_PROMPT_FLUSH_T880,CC_PROMPT_FLUSH_T880) | 25
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | ResourceManager | C01_CustomLogicIn | This routine has no source key protection. It is meant to be used for troubleshooting or temporary patching until permanent logic can be implemented. | NOP() | 0
RCOMMENT | ResourceManager | C02_CustomLogicOut | This routine has no source key protection. It is meant to be used for troubleshooting or temporary patching until permanent logic can be implemented. | NOP() | 0
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | System_Status | CLx_Status | ALARMS FOR LOCAL RACK AND REMOTE RACKS | OTE(CLx_SysStatus.Remote_7_CommFault) | 28
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_CoFeed_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_CoFeed_V3:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_CoFeed_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 8
RCOMMENT | AA_CoFeed_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 13
RCOMMENT | AA_CoFeed_V3:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 16
RCOMMENT | AA_CoFeed_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 49
RCOMMENT | AA_CoFeed_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 50
RCOMMENT | AA_CoFeed_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 51
RCOMMENT | AA_CoFeed_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_CoFeed_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 70
RCOMMENT | AA_CoFeed_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Monitor Deliveries To Determine If Either Delivery Is a Co-Feed & Issue The Start Command$N | OTL(UDT.CMD.Start) | 87
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Restart From Held$N | OTL(UDT.CMD.Start) | 88
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Go To Holding States When One Of The Active Deliveries Go To Held$N | OTL(UDT.WRK.UserHold) | 89
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 175
RCOMMENT | AA_CoFeed_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 176
RCOMMENT | AA_CoFeed_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 179
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_CoFeed_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_CoFeed_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_CoFeed_V4:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 8
RCOMMENT | AA_CoFeed_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 13
RCOMMENT | AA_CoFeed_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 16
RCOMMENT | AA_CoFeed_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 49
RCOMMENT | AA_CoFeed_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 50
RCOMMENT | AA_CoFeed_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 51
RCOMMENT | AA_CoFeed_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_CoFeed_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 70
RCOMMENT | AA_CoFeed_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Monitor Deliveries To Determine If Either Delivery Is a Co-Feed & Issue The Start Command$N | OTL(UDT.CMD.Start) | 87
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Restart From Held$N | OTL(UDT.CMD.Start) | 88
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Go To Holding States When One Of The Active Deliveries Go To Held$N | OTL(UDT.WRK.UserHold) | 89
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 177
RCOMMENT | AA_CoFeed_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 178
RCOMMENT | AA_CoFeed_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 181
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Monitor When Source Has Changed | OTL(UDT.WRK.SourceTankChanged) | 5
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Monitor When Alternate Path Has Changed | OTL(UDT.WRK.AltPathChanged) | 6
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Initialize Copy SourceInfo Instruction | OTU(UDT.WRK.SourceInfoStorageCopyComplete) | 7
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Verify Source & Destination Are Valid$NLoad SourceInfo & SourceProp | OTL(UDT.WRK.SourceSelected) | 8
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | TIMER PRESETS | MUL(UDT.Source.Info.PumpAllLowTime,1000,UDT.WRK.tmrPumpAllAutoEnd.PRE) | 12
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 13
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Nothing To Do$NJump To End$N | JMP(label_1) | 24
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Clear Registers When ClearSource Command Is Issued Or When AltPath Has Changed | OTU(SourceTankInst.DN) | 25
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 27
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 30
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 83
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 84
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 85
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 107
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 108
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 114
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | These Were Originally Only Allowed In State 30 But Were Moved to Allow Manipulation During Active Delivery | MOV(UDT.Source.Info.FlowSPDribble,UDT.VAL.DribbleRateSetpoint) | 145
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 323
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 324
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 327
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Monitor When Source Has Changed | OTL(UDT.WRK.SourceTankChanged) | 5
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Monitor When Alternate Path Has Changed | OTL(UDT.WRK.AltPathChanged) | 6
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Initialize Copy SourceInfo Instruction | OTU(UDT.WRK.SourceInfoStorageCopyComplete) | 7
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Verify Source & Destination Are Valid$NLoad SourceInfo & SourceProp | OTL(UDT.WRK.SourceSelected) | 8
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | TIMER PRESETS | MUL(UDT.Source.Info.PumpAllLowTime,1000,UDT.WRK.tmrPumpAllAutoEnd.PRE) | 12
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 13
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Nothing To Do$NJump To End$N | JMP(label_1) | 24
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Clear Registers When ClearSource Command Is Issued Or When AltPath Has Changed | OTU(SourceTankInst.DN) | 25
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 27
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 30
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 83
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 84
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 85
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 107
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 108
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 114
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | These Were Originally Only Allowed In State 30 But Were Moved to Allow Manipulation During Active Delivery | MOV(UDT.Source.Info.PumpSpeed,UDT.VAL.PumpSpeed) | 145
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 338
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 339
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 342
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_INERT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_INERT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | AA_INERT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | AA_INERT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | AA_INERT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | AA_INERT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | AA_INERT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Path_CMD_Energize) | 65
RCOMMENT | AA_INERT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_INERT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 70
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 10
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 11
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 16
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 17
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 18
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 30
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 54
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 55
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 71
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 72
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 78
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 83
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.Mode,UDT.VAL.Mode) | 84
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 86
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 108
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 114
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 115
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1400,UDT.SET.NextStateNumber) | 116
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 117
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 118
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 122
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NPRS Cook Mode (Pressure Cook)$N**************************** | MOV(1410,UDT.SET.NextStateNumber) | 126
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NBleed Mode$N**************************** | MOV(1510,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 135
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 171
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 6
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 7
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 12
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 13
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 14
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 27
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 51
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 52
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 71
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 72
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 78
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 83
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTL(UDT.WRK.ModeChange) | 84
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 88
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 110
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 117
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 118
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NVacuum Pump Mode Selected$N*************************** | MOV(1600,UDT.SET.NextStateNumber) | 119
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 121
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 125
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NVac Pump Mode$N**************************** | MOV(1610,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Control of Primary Pump | NOP() | 134
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.PrimBypassValve_CMD_Open) | 137
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 138
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NPrimary Vacuum Pump Control$N******************* | OTE(VacPump.CMD.AutoStop) | 162
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NPrimaryVacuum Pump Bypass Valve Control$N******************* | MOV(0,VacBypassValve.SET.FullRate) | 163
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 176
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_PRS_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_PRS_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_PRS_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_PRS_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_PRS_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_PRS_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 57
RCOMMENT | AA_PRS_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 58
RCOMMENT | AA_PRS_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 77
RCOMMENT | AA_PRS_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 78
RCOMMENT | AA_PRS_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_PRS_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_PRS_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.Mode,UDT.VAL.Mode) | 90
RCOMMENT | AA_PRS_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 94
RCOMMENT | AA_PRS_V1:AOI | Logic | Change Mode$N | MOV(UDT.VAL.Mode,UDT.SET.Mode) | 116
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 122
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NScrub Mode Selected$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 124
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NVacuum Pump Mode Selected$N*************************** | MOV(1600,UDT.SET.NextStateNumber) | 125
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 126
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NScrub Mode$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 134
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NVac Pump Mode$N**************************** | MOV(1620,UDT.SET.NextStateNumber) | 141
RCOMMENT | AA_PRS_V1:AOI | Logic | When Primary Pump is selected | MOV(UDT.WRK.PrimVacModePathID,UDT.WRK.HDR1_ReqPath) | 142
RCOMMENT | AA_PRS_V1:AOI | Logic | When Secondary Pump is selected | MOV(UDT.WRK.SecVacModePathID,UDT.WRK.HDR1_ReqPath) | 143
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary vacuum Header | NOP() | 145
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Pump | NOP() | 153
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.PrimBypassValve_CMD_Open) | 156
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Secondary vacuum Header | NOP() | 157
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Secondary Pump | NOP() | 161
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.SecBypassValve_CMD_Open) | 163
RCOMMENT | AA_PRS_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 164
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NPrimary Vacuum Pump Control$N******************* | OTE(PrimVacPump.CMD.AutoStop) | 188
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NSecondary Vacuum Pump Control$N******************* | OTE(SecVacPump.CMD.AutoStop) | 189
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NPrimaryVacuum Pump Bypass Valve Control$N******************* | MOV(0,PrimVacBypassValve.SET.FullRate) | 190
RCOMMENT | AA_PRS_V1:AOI | Logic | Secondary Vacuum Pump Bypass Valve Control$N******************* | MOV(0,SecVacBypassValve.SET.FullRate) | 191
RCOMMENT | AA_PRS_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 205
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 3
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | OTE(UDT.WRK.NotInUse) | 23
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | Disable if not enabled | JMP(Disabled) | 24
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 28
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 38
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.Enable) | 39
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 41
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 69
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 70
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 71
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 81
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 82
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 88
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 95
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 157
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 160
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 11
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 12
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 17
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 18
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 19
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 31
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 58
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 59
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 86
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 87
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 93
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 98
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 99
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 101
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | This was Temp Override and Overcome. This was Removed | MOV(1000,UDT.SET.NextStateNumber) | 124
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 131
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 137
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 138
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 139
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(0,UDT.WRK.ValveRequest) | 140
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(0,UDT.WRK.LastMode) | 147
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 151
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 154
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 175
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Jacket Coils Configuration | CPT(UDT.WRK.ReqPath,32) | 187
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 198
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 135
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | AEA - To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 151
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 153
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 157
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 162
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 183
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 189
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 190
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 191
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 192
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 193
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 194
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 195
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 210
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 135
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | AEA - To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 150
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1500,UDT.SET.NextStateNumber) | 152
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1500,UDT.SET.NextStateNumber) | 156
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Aborting Shut down sequence | NOP() | 161
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 182
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 188
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 189
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 190
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 191
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 192
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 193
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 194
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 209
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 132
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 147
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 152
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 154
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 158
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 163
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 184
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 190
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 191
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 192
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 193
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 194
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 195
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 196
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 211
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_VENT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_VENT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | AA_VENT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | AA_VENT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | AA_VENT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | AA_VENT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | AA_VENT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Path_CMD_Energize) | 65
RCOMMENT | AA_VENT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_VENT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 70
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 1
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | CM_AIN_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AIN_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 2
RCOMMENT | CM_AIN_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.LoTimer.PRE,1000,UDT.CFG.LoFaultTime) | 6
RCOMMENT | CM_AIN_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 7
RCOMMENT | CM_AIN_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 8
RCOMMENT | CM_AIN_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 9
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 16
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 17
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 18
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 19
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.FLT.Overrange) | 20
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.HiHi) | 21
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 22
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.LoLo) | 23
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 24
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 25
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Calibration Fault | OTL(UDT.FLT.CalFault) | 26
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Underrange | OTL(UDT.FLT.Underrange) | 27
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Overrange | OTL(UDT.FLT.Overrange) | 28
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 30
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 31
RCOMMENT | CM_AIN_V3:AOI | Logic | VALUE: Analog Input | MOV(UDT.SET.SIM_Value,UDT.VAL.ActualScaled) | 34
RCOMMENT | CM_AIN_V3:AOI | Logic | VALUE: Analog Input | MOV(UDT.VAL.ActualFiltered,UDT.WRK.FilteredLast_Scan) | 35
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 39
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 40
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 5 In Use | MOV(5,UDT.VAL.HMIState) | 41
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 5 Normal Conditions Not In Use | MOV(6,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AIN_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 43
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 44
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(IN_SuppressLevelAlarms) | 45
RCOMMENT | CM_AIN_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 46
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 47
RCOMMENT | CM_AIN_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 48
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 1
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 2
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 5
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_AOD_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 6
RCOMMENT | CM_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 11
RCOMMENT | CM_AOD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 18
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 19
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 20
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_AOD_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 24
RCOMMENT | CM_AOD_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 25
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 28
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 29
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 32
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 33
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 41
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUN | MOV(3,UDT.VAL.HMIState) | 43
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL OFF | MOV(4,UDT.VAL.HMIState) | 44
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUN | MOV(5,UDT.VAL.HMIState) | 45
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO OFF | MOV(6,UDT.VAL.HMIState) | 46
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 49
RCOMMENT | CM_AOD_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 50
RCOMMENT | CM_AOD_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 51
RCOMMENT | CM_AOD_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 52
RCOMMENT | CM_AOD_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 53
RCOMMENT | CM_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 54
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.SET.ManSetpoint,UDT.VAL.CVScaled) | 1
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | MESSAGES: Analog Output | MOV(UDT.OUT.CV,OUT_CV) | 2
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 3
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 4
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 5
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_AOUT_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_AOUT_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(Disabled) | 9
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 17
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 18
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 19
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 20
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_AOUT_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.Opened) | 24
RCOMMENT | CM_AOUT_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.Closed) | 25
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 26
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 28
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 30
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 31
RCOMMENT | CM_AOUT_V3:AOI | Logic | VALUE: CV Calculation | MOV(100,UDT.SET.ManSetpoint) | 35
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR COMMANDS | MOV(UDT.OUT.CV,OUT_CV) | 36
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 2 FAULT ACKNOWLEDGE | MOV(2,UDT.VAL.HMIState) | 43
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 44
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 45
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 46
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 47
RCOMMENT | CM_AOUT_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 48
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 49
RCOMMENT | CM_AOUT_V3:AOI | Logic | MESSAGES: Analog Output | MOV(UDT.OUT.CV,OUT_CV) | 51
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 53
RCOMMENT | CM_AOUT_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 54
RCOMMENT | CM_AOUT_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 55
RCOMMENT | CM_AOUT_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 56
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 1
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_DIFF_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DIFF_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 2
RCOMMENT | CM_DIFF_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.LoTimer.PRE,1000,UDT.CFG.LoFaultTime) | 6
RCOMMENT | CM_DIFF_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 7
RCOMMENT | CM_DIFF_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 8
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 15
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 16
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 17
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 18
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.FLT.HiHi) | 19
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.HiHi) | 20
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 21
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.LoLo) | 22
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 23
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Primary Device Is Faulted of Not Enabled$N | OTL(UDT.FLT.HighRefDevice) | 24
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Secondary Device Is Faulted of Not Enabled$N | OTL(UDT.FLT.LowRefDevice) | 25
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 27
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 28
RCOMMENT | CM_DIFF_V3:AOI | Logic | Move & Calculate Values$N | SUB(UDT.VAL.HighRefActual,UDT.VAL.LowRefActual,UDT.VAL.Differential) | 31
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 36
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 37
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 5 NORMAL CONDITIONS | MOV(5,UDT.VAL.HMIState) | 38
RCOMMENT | CM_DIFF_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 39
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 40
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 41
RCOMMENT | CM_DIFF_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 42
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DIFF_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Unlatch) | 1
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | CM_DI_V5:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DI_V5:AOI | Logic | TIMER PRESETS | MOV(1000000,UDT.WRK.Cycle_Counter.PRE) | 8
RCOMMENT | CM_DI_V5:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 9
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 16
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 17
RCOMMENT | CM_DI_V5:AOI | Logic | Delay Timer: Signal Delay Timer | RES(UDT.WRK.Delay_ON) | 19
RCOMMENT | CM_DI_V5:AOI | Logic | STATUS: Actual Digital Status | OTE(UDT.STS.Actual) | 23
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 24
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 25
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Reset Faults$N | OTU(ZoneLink.FaultExists) | 26
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.InputCard) | 27
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 28
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Is Fault$N | OTL(UDT.FLT.InputIsFault) | 29
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Generate Fault Code$N | OTL(UDT.STS.Faulted) | 35
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 36
RCOMMENT | CM_DI_V5:AOI | Logic | STATUS: Simulation Mode Status | OTE(STS_SIM) | 40
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: Faulted$N | MOV(1,UDT.VAL.HMIState) | 41
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: Warning$N | MOV(2,UDT.VAL.HMIState) | 42
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 5 INPUT ON | MOV(5,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 6 INPUT OFF | MOV(6,UDT.VAL.HMIState) | 44
RCOMMENT | CM_DI_V5:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 45
RCOMMENT | CM_DI_V5:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.FLT.FaultCode) | 46
RCOMMENT | CM_DI_V5:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Unlatch) | 47
RCOMMENT | CM_DI_V5:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 48
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 49
RCOMMENT | CM_DI_V5:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 50
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DOUT_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_DOUT_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 6
RCOMMENT | CM_DOUT_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 11
RCOMMENT | CM_DOUT_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 18
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 19
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 20
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_DOUT_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.ON) | 24
RCOMMENT | CM_DOUT_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.OFF) | 25
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 28
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 29
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 34
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 35
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 44
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUN | MOV(3,UDT.VAL.HMIState) | 45
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL OFF | MOV(4,UDT.VAL.HMIState) | 46
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUN | MOV(5,UDT.VAL.HMIState) | 47
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO OFF | MOV(6,UDT.VAL.HMIState) | 48
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 51
RCOMMENT | CM_DOUT_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 52
RCOMMENT | CM_DOUT_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 53
RCOMMENT | CM_DOUT_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 54
RCOMMENT | CM_DOUT_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Output) | 55
RCOMMENT | CM_DOUT_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 56
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Running Status | TOF(UDT.WRK.tmrRunning,0,0) | 5
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | MOV(IN_Cycle_CountB,UDT.IN.Cycle_CountB) | 6
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS$N | MOV(0.0,UDT.IN.Pressure_Indicator) | 7
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth_Cycle) | 8
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTU(UDT.IN.InputHealth_Pressure) | 9
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.OutputCardHealth) | 10
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 13
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 14
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | TIMER PRESETS | DIV(tmrPairStartDelay.PRE,1000,UDT.CFG.PairStopDelay) | 17
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CPT(UDT.VAL.ScaledPressure,UDT.CFG.EngPressureLow+((UDT.IN.Pressure_Indicator-UDT.CFG.RawPressureLow)/(UDT.CFG.RawPressureHigh-UDT.CFG.RawPressureLow)*(UDT.CFG.EngPressureHigh-UDT.CFG.EngPressureLow))) | 25
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CLR(UDT.VAL.ScaledPressure) | 26
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | Input: Mass Flow Rate | MOV(UDT.WRK.tmrFlowRateAcc.ACC,UDT.WRK.nFlowRatePreviousTime) | 27
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CALCULATE DELTA | CLR(UDT.WRK.CurrentSampleCycles) | 28
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CLR(UDT.VAL.CyclesPerMinB) | 29
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.Interlock) | 34
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 35
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 36
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 38
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 39
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.CyclesEmptyThreshold) | 42
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.Empty) | 43
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.bWorkingFailedtoRun) | 44
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Stop Check | OTE(UDT.WRK.bWorkingFailedtoStop) | 45
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 46
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Run, Failed to Stop | OTL(UDT.FLT.FailedToStop) | 47
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 48
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Cycle Counter input Card$N | OTL(UDT.FLT.InputCard_Cycle) | 49
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Pressure Indicator input Card$N | OTL(UDT.FLT.InputCard_Pressure) | 50
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 51
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDInMan) | 52
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Fault Code Generation | OTU(UDT.WRK.bWorkingRunCmd) | 56
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 57
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 62
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.CMD.RunTimeReset) | 69
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 1 Faulted | MOV(1,UDT.VAL.HMIState) | 71
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 2 Warning | MOV(2,UDT.VAL.HMIState) | 72
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 73
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 74
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 75
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 76
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 0 DISABLED | MOV(0,UDT.VAL.HMIState) | 77
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 79
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Control.LogicDefinedPt00Data) | 3
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_HI4050_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_HI4050_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_HI4050_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_HI4050_V3:AOI | Logic | Sequence for reading a floating point from Scale transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 5
RCOMMENT | CM_HI4050_V3:AOI | Logic | A/D Conversion Error or A/D Failure$N | OTL(UDT.FLT.Custom.0) | 12
RCOMMENT | CM_HI4050_V3:AOI | Logic | Center Of Zero | OTL(UDT.FLT.Custom.1) | 13
RCOMMENT | CM_HI4050_V3:AOI | Logic | Weight Overrange$N | OTL(UDT.FLT.Custom.2) | 14
RCOMMENT | CM_HI4050_V3:AOI | Logic | Real Time Clock Failure$N | OTL(UDT.FLT.Custom.3) | 15
RCOMMENT | CM_HI4050_V3:AOI | Logic | SD Card Read/Write Error$N | OTL(UDT.FLT.Custom.4) | 16
RCOMMENT | CM_HI4050_V3:AOI | Logic | Motion Error$N | OTL(UDT.FLT.Custom.5) | 17
RCOMMENT | CM_HI4050_V3:AOI | Logic | Display Error$N | OTL(UDT.FLT.Custom.6) | 18
RCOMMENT | CM_HI4050_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 22
RCOMMENT | CM_HI4050_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 23
RCOMMENT | CM_HI4050_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 24
RCOMMENT | CM_HI4050_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 25
RCOMMENT | CM_HI4050_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 26
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_HI6500_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_HI6500_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_HI6500_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_HI6500_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 12
RCOMMENT | CM_HI6500_V3:AOI | Logic | A/D Conversion Error or A/D Failure$N | OTL(UDT.FLT.Custom.0) | 14
RCOMMENT | CM_HI6500_V3:AOI | Logic | Center Of Zero | OTU(UDT.FLT.Custom.1) | 15
RCOMMENT | CM_HI6500_V3:AOI | Logic | Weight Overrange$N | OTU(UDT.FLT.Custom.2) | 16
RCOMMENT | CM_HI6500_V3:AOI | Logic | Real Time Clock Failure$N | OTU(UDT.FLT.Custom.3) | 17
RCOMMENT | CM_HI6500_V3:AOI | Logic | SD Card Read/Write Error$N | OTL(UDT.FLT.Custom.4) | 18
RCOMMENT | CM_HI6500_V3:AOI | Logic | Motion Error$N | OTU(UDT.FLT.Custom.5) | 19
RCOMMENT | CM_HI6500_V3:AOI | Logic | Display Error$N | OTU(UDT.FLT.Custom.6) | 20
RCOMMENT | CM_HI6500_V3:AOI | Logic | Test In Progress | OTL(UDT.FLT.Custom.7) | 21
RCOMMENT | CM_HI6500_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 27
RCOMMENT | CM_HI6500_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 28
RCOMMENT | CM_HI6500_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 29
RCOMMENT | CM_HI6500_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 30
RCOMMENT | CM_HI6500_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_IND560E_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_IND560E_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_IND560E_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_IND560E_V3:AOI | Logic | Sequence for reading a floating point from IND560 transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 9
RCOMMENT | CM_IND560E_V3:AOI | Logic | Update the Command to the IND570$N$NThe IND570 only acts on a command if it sees a change from the previous command. That means if you need to send another Tare after the first Tare, there must be another command between them - such as Display Net Weight.$N$NThis rung waits until the comand changes, then it writes the Command, and the Command Data to the PLC$'s output buffer to the IND570. It then updates the history.$N$NNote that the MOV command that moves Command_Data to Command_Data is used to display or modify the value easily. This move can be deleted from your program.$N$N | MOV(Command,CommandPrev) | 16
RCOMMENT | CM_IND560E_V3:AOI | Logic | Various example commands$N$N$NThis rung allows triggering of some sample commands to the IND570. Your own logic does not need to function this way. It only needs to write a value to $QCommand$Q, and if necessary, to $QCommand_Data.$Q $N$NThe MOV instruction for FloatingPoint_Data is only so that the returned data is easy to read after one of the command bits has been set.$N$NOther commands that can be sent to the IND570 can be found in $Nthe PLC Interface Manual.$N$N | MOV(11,Command) | 17
RCOMMENT | CM_IND560E_V3:AOI | Logic | $NMap the Floating Point Input Indicator bits into a word so we can decode what type of data the IND570 is currently returning to us. See in the PLC Inteface Manual for a mapping of these values.$N$N | MOV(-1,DataReturned) | 18
RCOMMENT | CM_IND560E_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 19
RCOMMENT | CM_IND560E_V3:AOI | Logic | Scale Controller Is Powering-Up or In Config Mode | OTL(UDT.FLT.Custom.1) | 22
RCOMMENT | CM_IND560E_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 27
RCOMMENT | CM_IND560E_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 28
RCOMMENT | CM_IND560E_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 29
RCOMMENT | CM_IND560E_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 30
RCOMMENT | CM_IND560E_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_IND570E_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_IND570E_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_IND570E_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_IND570E_V3:AOI | Logic | Sequence for reading a floating point from IND560 transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 7
RCOMMENT | CM_IND570E_V3:AOI | Logic | Update the Command to the IND570$N$NThe IND570 only acts on a command if it sees a change from the previous command. That means if you need to send another Tare after the first Tare, there must be another command between them - such as Display Net Weight.$N$NThis rung waits until the comand changes, then it writes the Command, and the Command Data to the PLC$'s output buffer to the IND570. It then updates the history.$N$NNote that the MOV command that moves Command_Data to Command_Data is used to display or modify the value easily. This move can be deleted from your program.$N$N | MOV(Command,CommandPrev) | 14
RCOMMENT | CM_IND570E_V3:AOI | Logic | Various example commands$N$N$NThis rung allows triggering of some sample commands to the IND570. Your own logic does not need to function this way. It only needs to write a value to $QCommand$Q, and if necessary, to $QCommand_Data.$Q $N$NThe MOV instruction for FloatingPoint_Data is only so that the returned data is easy to read after one of the command bits has been set.$N$NOther commands that can be sent to the IND570 can be found in $Nthe PLC Interface Manual.$N$N | MOV(11,Command) | 15
RCOMMENT | CM_IND570E_V3:AOI | Logic | $NMap the Floating Point Input Indicator bits into a word so we can decode what type of data the IND570 is currently returning to us. See in the PLC Inteface Manual for a mapping of these values.$N$N | MOV(-1,DataReturned) | 16
RCOMMENT | CM_IND570E_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 17
RCOMMENT | CM_IND570E_V3:AOI | Logic | Scale Controller Is Powering-Up or In Config Mode | OTL(UDT.FLT.Custom.1) | 20
RCOMMENT | CM_IND570E_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 25
RCOMMENT | CM_IND570E_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 26
RCOMMENT | CM_IND570E_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 27
RCOMMENT | CM_IND570E_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 28
RCOMMENT | CM_IND570E_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 29
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Stop) | 3
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 3
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoStop) | 1
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 3
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 9
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 10
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 11
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(5000,UDT.WRK.tmrIllegalHOA.PRE) | 33
RCOMMENT | CM_M2S_V3:AOI | Logic | VAL.InUseBy is a DINT array that contains Integers values of the $'owners$' of this CM$N$N | RES(UDT.WRK.InUseResltCntrl) | 40
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Pre-Processing Stop PB In Auto Running | OTE(UDT.WRK.StopPBWhileRunAuto) | 41
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Hand Operation Start & Stop$N | OTU(UDT.WRK.bInternalRun) | 42
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 43
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bInternalRun) | 44
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Hand Operation Start & Stop$N | OTU(UDT.WRK.bInternalRun) | 45
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop Transition Through Slow$N | OTL(UDT.STS.StopTransitioning) | 46
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER: Stop Transitioning Maintain Timer | OTU(UDT.STS.StopTransitioning) | 47
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Single Speed Run$N | OTU(UDT.STS.Fast) | 48
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Fast-Slow Speed Motor Command Processing$N | OTL(UDT.STS.Fast) | 49
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Forward-Reverse Motor Command Processing$N | OTL(UDT.STS.Reverse) | 50
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop / OFF Command Processing$N | OTU(UDT.WRK.bInternalRun) | 51
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 52
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 53
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.RunTimeFault) | 54
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Overload | OTE(UDT.STS.Overload) | 55
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Disconnect | OTE(UDT.STS.Disconnect) | 56
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 57
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 60
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Ramp (Stopping) Status | OTE(UDT.STS.Stopping) | 61
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.FailingToStart) | 65
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Stop Check | OTE(UDT.WRK.FailingToStop) | 66
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.FailingToStartTransition) | 67
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrMotorTransition,5000,0) | 68
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run, Failed to Stop | OTU(ExternalFault) | 69
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Overload) | 70
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Stop PB Pressed While Running In Auto | OTL(UDT.FLT.StopPBInAuto) | 71
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 72
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 73
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 82
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop Transition Through Slow After Fault | OTL(UDT.STS.StopTransitioning) | 86
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Start Transition Through Slow$N | OTL(UDT.STS.StartTransitioning) | 87
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 1$NFAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 95
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 96
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 3$NMANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 97
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 4$NMANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 98
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 5$NAUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 99
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 6$NAUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 100
RCOMMENT | CM_M2S_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 101
RCOMMENT | CM_M2S_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 104
RCOMMENT | CM_M2S_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoStart) | 105
RCOMMENT | CM_M2S_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 106
RCOMMENT | CM_M2S_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 107
RCOMMENT | CM_M2S_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 108
RCOMMENT | CM_M2S_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 109
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METDG_V3:AOI | Logic | CM Type ID$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METDG_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METDG_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METDG_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METDG_V3:AOI | Logic | Fault: Message to pull fault word from the meter. | MSG(MSG_Alarms) | 11
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 12
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: NVError | OTL(UDT.FLT.Custom.0) | 14
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: RAM Error | OTL(UDT.FLT.Custom.1) | 15
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: RTI Failure | OTL(UDT.FLT.Custom.2) | 16
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Sensor Failure | OTL(UDT.FLT.Custom.3) | 17
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Temperature Range | OTL(UDT.FLT.Custom.4) | 18
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Other Failure | OTL(UDT.FLT.Custom.5) | 19
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Trans Intializing | OTL(UDT.FLT.Custom.6) | 20
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Meter SIM Is ON | OTL(UDT.FLT.Custom.7) | 21
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Watchdog Error$N | OTL(UDT.FLT.Custom.8) | 22
RCOMMENT | CM_METDG_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 26
RCOMMENT | CM_METDG_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_VolTotal,UDT.INOUT.VolumeTotal) | 28
RCOMMENT | CM_METDG_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 29
RCOMMENT | CM_METDG_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 30
RCOMMENT | CM_METDG_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 31
RCOMMENT | CM_METDG_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 32
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoEnable[0],CMDSize) | 1
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METP4_V3:AOI | Logic | Program Name: Totalize_Freq$NRoutine Name: Totalize_Freq$NDescription: Totalizer Device Control Module$NVariation: For Use With Pulse Module (IP4) | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METP4_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METP4_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METP4_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METP4_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | ADD(UDT.INOUT.RolloverCountVol,1,UDT.INOUT.RolloverCountVol) | 13
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_MassTotal,(UDT.INOUT.RolloverCountMass*UDT.CFG.RollOverMass)+UDT.INOUT.MassTotal) | 14
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.MassTotal,localPrevMassTotal) | 15
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_VolTotal,(UDT.INOUT.RolloverCountVol*UDT.CFG.RollOverVolume) + UDT.INOUT.VolumeTotal) | 16
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 17
RCOMMENT | CM_METP4_V3:AOI | Logic | FAULT: Control Module Fault | OTE(STS_InUse) | 19
RCOMMENT | CM_METP4_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 23
RCOMMENT | CM_METP4_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 25
RCOMMENT | CM_METP4_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 26
RCOMMENT | CM_METP4_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 27
RCOMMENT | CM_METP4_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 28
RCOMMENT | CM_METP4_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 29
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METPAIR_V3:AOI | Logic | Find the UserID of the Currently Connected User | RES(InUseResltCntrl) | 10
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METPG_V3:AOI | Logic | Program Name: MPG$NDescription: Totalizer Device Control Module$NVariation: For Use With Pulse Module (IP4) | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METPG_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METPG_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METPG_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METPG_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | ADD(UDT.INOUT.RolloverCountVol,1,UDT.INOUT.RolloverCountVol) | 15
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_MassTotal,(UDT.INOUT.RolloverCountMass*UDT.CFG.RollOverMass)+UDT.INOUT.MassTotal) | 16
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.MassTotal,localPrevMassTotal) | 17
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_VolTotal,(UDT.INOUT.RolloverCountVol*UDT.CFG.RollOverVolume) + UDT.INOUT.VolumeTotal) | 18
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 19
RCOMMENT | CM_METPG_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 21
RCOMMENT | CM_METPG_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_RawVolume,UDT.INOUT.VolumeTotal) | 23
RCOMMENT | CM_METPG_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 24
RCOMMENT | CM_METPG_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 25
RCOMMENT | CM_METPG_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 26
RCOMMENT | CM_METPG_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 27
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Density | MOV(UDT.IN.Density,UDT.VAL.Density) | 1
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Total | ADD(UDT.IN.VolumeTotal,UDT.SET.SIMDeltaPerScanVolume,UDT.IN.VolumeTotal) | 2
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow | MOV(UDT.IN.MassFlow,UDT.VAL.MassFlowRate) | 3
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow | MOV(UDT.IN.VolumeFlow,UDT.VAL.VolumeFlowRate) | 4
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Temperature | MOV(UDT.IN.Temp,UDT.VAL.Temp) | 5
RCOMMENT | CM_MET_V3:AOI | Logic | Value: DriveGain | COP(IN_DriveGain,UDT.VAL.DriveGain,1) | 6
RCOMMENT | CM_MET_V3:AOI | Logic | INPUT: Zone Link Interlock Status$N | OTE(UDT.IN.Interlock) | 8
RCOMMENT | CM_MET_V3:AOI | Logic | INPUT: ZoneLink ID #$N | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 9
RCOMMENT | CM_MET_V3:AOI | Logic | Value: Calculated Volumeteric Flow Rate | MOV(0,UDT.VAL.VolumeFlowRate) | 10
RCOMMENT | CM_MET_V3:AOI | Logic | TIMER PRESETS | MOV(1000000,tmrVolumeFlowRateAcc.PRE) | 11
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | RES(InUseResltCntrl) | 17
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | RES(tmrLowDensity) | 20
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | RES(tmrLowDensity) | 21
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 22
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 23
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto/Manual Zero | MOV(UDT.SET.Preact,UDT.VAL.Preact) | 24
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto/Manual Zero | DIV(UDT.INOUT.MassTotal,UDT.VAL.Density,UDT.IN.VolumeTotal) | 25
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Settle | OTL(UDT.STS.SettleComplete) | 26
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS: Totalizer Complete$NACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 28
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Stop | OTL(UDT.STS.Stopping) | 29
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Stabilize | OTU(UDT.STS.SettleComplete) | 30
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.HiDensity) | 31
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: HI/LO Fault Timer | TON(tmrLowFlow,?,?) | 32
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoFlow) | 33
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Denisty Low Fault Timer | TON(tmrLowDensity,?,?) | 34
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoDensity) | 35
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Denisty Hi Fault Timer | TON(tmrHiDensity,?,?) | 36
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.HiDensity) | 37
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 38
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Auto Command While In Manual$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 39
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Stopping) | 46
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 47
RCOMMENT | CM_MET_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 50
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.MassFlowRate) | 51
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.IN.MassTotal,rTotalPreviousScan_Mass) | 52
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | CLR(rTotalSinceInit_Mass) | 53
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.VolumeFlowRate) | 54
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.IN.VolumeTotal,rTotalPreviousScan_VOL) | 55
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | CLR(rTotalSinceInit_VOL) | 56
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.MassTotal,UDT.VAL.AmountRemain) | 57
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.VolumeTotal,UDT.VAL.AmountRemain) | 58
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Temperature | MOV(UDT.IN.Temp,UDT.VAL.Temp) | 59
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.STS.InUse) | 60
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 1 | MOV(1,UDT.VAL.HMIState) | 65
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 1 | MOV(2,UDT.VAL.HMIState) | 66
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 3 | MOV(3,UDT.VAL.HMIState) | 67
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 68
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 5 | MOV(5,UDT.VAL.HMIState) | 69
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 70
RCOMMENT | CM_MET_V3:AOI | Prescan | CALCULATE DELTA | OTL(UDT.STS.Stopping) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | CM Type ID$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 5
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 13
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: NVError | OTL(UDT.FLT.Custom.0) | 15
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: RAM Error | OTL(UDT.FLT.Custom.1) | 16
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: RTI Failure | OTL(UDT.FLT.Custom.2) | 17
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Sensor Failure | OTL(UDT.FLT.Custom.3) | 18
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Temperature Range | OTL(UDT.FLT.Custom.4) | 19
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Other Failure | OTL(UDT.FLT.Custom.5) | 20
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Trans Intializing | OTL(UDT.FLT.Custom.6) | 21
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Meter SIM Is ON | OTL(UDT.FLT.Custom.7) | 22
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Watchdog Error$N | OTL(UDT.FLT.Custom.8) | 23
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Comm Loss$N | OTL(UDT.FLT.Custom.9) | 24
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Tube Not Full or Drive Overrange$N | OTL(UDT.FLT.Custom.10) | 25
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Mass Flow Overrange OR Density Overrange | OTL(UDT.FLT.Custom.11) | 26
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 29
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_Status.Totalizer_2,UDT.INOUT.VolumeTotal) | 31
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 34
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 35
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 36
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 37
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_ControlValue) | 4
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 4
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrLoopOscillating.PRE,1000,UDT.CFG.OscillationDelayTime) | 8
RCOMMENT | CM_PID_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | MOV(UDT.CFG.EngMax,PIDLoop.MAXTIE) | 12
RCOMMENT | CM_PID_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 13
RCOMMENT | CM_PID_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 14
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 15
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(IN_Setpoint,PIDLoop.SP) | 16
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 17
RCOMMENT | CM_PID_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 18
RCOMMENT | CM_PID_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 19
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 20
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 21
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 22
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 23
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 24
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 25
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 26
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrFaultDelay.PRE,1000,UDT.CFG.FaultDelayTime) | 30
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 37
RCOMMENT | CM_PID_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 40
RCOMMENT | CM_PID_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 41
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 42
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 43
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 44
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OscillationDeviation) | 46
RCOMMENT | CM_PID_V3:AOI | Logic | VALUE Deviation Limit Values | SUB(PIDLoop.SP,UDT.CFG.AlarmDeviation,UDT.VAL.LoLoDeviation) | 47
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Loop in Control | OTL(UDT.STS.InControl) | 48
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Loop Out of Control | OTU(UDT.STS.InControl) | 49
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Oscillation of PV | OTE(UDT.STS.Oscillating) | 50
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.LoLoDeviation) | 51
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HIHI/LOLO Deviation Fault Timer | TON(UDT.WRK.tmrWarningDelay,0,499) | 52
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HI/LO Fault Timer | TON(UDT.WRK.tmrAlarmDelay,0,0) | 53
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HIHI Deviation | OTL(UDT.FLT.HiHiDeviation) | 54
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HI Deviation | OTE(UDT.FLT.HiDeviation) | 55
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Lo Deviation | OTE(UDT.FLT.LoDeviation) | 56
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Lo Lo Deviation | OTL(UDT.FLT.LoLoDeviation) | 57
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Oscillation in PV | OTL(UDT.FLT.OscillationDeviation) | 58
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 59
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 60
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.WRK.bWorkingOpenValve) | 62
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 63
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 67
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 73
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 74
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 75
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 76
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 77
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 78
RCOMMENT | CM_PID_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 79
RCOMMENT | CM_PID_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 81
RCOMMENT | CM_PID_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 82
RCOMMENT | CM_PID_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 83
RCOMMENT | CM_PID_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 84
RCOMMENT | CM_PID_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(UDT.OUT.CV,OUT_ControlValue) | 85
RCOMMENT | CM_PID_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_ControlValue) | 86
RCOMMENT | CM_PID_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 87
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 1
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],UDT.WRK.CMDAutoZeroSize) | 2
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.OutputDisable) | 3
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_PMR_V3:AOI | Logic | Grundfos Metering Pump Estimated Delivery$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Zone Link Interlock Status$N | OTE(UDT.IN.Interlock) | 9
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Input Channel Health | OTE(UDT.IN.InHealth_PanelEstop) | 10
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Input Channel Health | OTE(UDT.IN.InHealth_PumpFault) | 11
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Output Channel Health | OTE(UDT.IN.OutputHealth) | 12
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: ZoneLink ID #$N | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 13
RCOMMENT | CM_PMR_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 14
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 21
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | OTU(UDT.STS.Complete) | 24
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | OTU(UDT.STS.Complete) | 25
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 26
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 27
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto/Manual Zero | RES(UDT.WRK.tmrTimedDelivery) | 28
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Stop | OTU(UDT.STS.Running) | 29
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 31
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.InputCard) | 32
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.OutputCard) | 33
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Auto Command While In Manual$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 34
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Pump Is Faulted$N | OTL(UDT.FLT.PumpFaulted) | 35
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 37
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 38
RCOMMENT | CM_PMR_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 41
RCOMMENT | CM_PMR_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.WRK.tmrElapsedAcc.ACC,UDT.WRK.nElapsedAccPrevious) | 42
RCOMMENT | CM_PMR_V3:AOI | Logic | STATUS: Totalizer Complete$NACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 44
RCOMMENT | CM_PMR_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.MassFlowRate) | 45
RCOMMENT | CM_PMR_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.MassTotal,UDT.VAL.AmountRemain) | 46
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(STS_InUse) | 47
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(1,UDT.VAL.HMIState) | 51
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 52
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 3 | MOV(3,UDT.VAL.HMIState) | 53
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 54
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 5 | MOV(5,UDT.VAL.HMIState) | 55
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 56
RCOMMENT | CM_PMR_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 57
RCOMMENT | CM_PMR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 59
RCOMMENT | CM_PMR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],UDT.WRK.CMDAutoZeroSize) | 60
RCOMMENT | CM_PMR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.OutputDisable) | 61
RCOMMENT | CM_PMR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 62
RCOMMENT | CM_PMR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 63
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_SF_V3:AOI | Logic | TIMER PRESETS | OTL(UDT.CFG.IsFault) | 0
RCOMMENT | CM_SF_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 2
RCOMMENT | CM_SF_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.Delay_OFF.PRE,1000,UDT.WRK.DelayAckActive.PRE) | 10
RCOMMENT | CM_SF_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 11
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 13
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT: Reset Faults$N | RES(UDT.WRK.DelayAckActive) | 14
RCOMMENT | CM_SF_V3:AOI | Logic | Delay Timer: Signal Delay Timer | TON(UDT.WRK.Delay_OFF,?,?) | 15
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Actual Digital Status | OTE(UDT.STS.Actual) | 19
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Actual Digital Status | OTL(UDT.FLT.SystemFault) | 21
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 24
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Simulation Mode Status | OTE(STS_SIM) | 28
RCOMMENT | CM_SF_V3:AOI | Logic | HMI Device Status: Faulted$N | MOV(1,UDT.VAL.HMIState) | 29
RCOMMENT | CM_SF_V3:AOI | Logic | HMI Device Status: STATE 5 INPUT ON | MOV(5,UDT.VAL.HMIState) | 30
RCOMMENT | CM_SF_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 31
RCOMMENT | CM_SF_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 32
RCOMMENT | CM_SF_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 33
RCOMMENT | CM_SF_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 34
RCOMMENT | CM_SF_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 35
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_SZONE_V3:AOI | EnableInFalse | ENABLE IN FALSE: Disable Interlock Output$N | MOV(0,UDT.VAL.HMIState) | 0
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Interlock Input$N | OTE(UDT.IN.Interlock) | 2
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Interlock Input Health$N | OTE(UDT.IN.InterlockHealth) | 3
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Reverse Operation Interlock$N | OTE(UDT.IN.RevInterlock) | 4
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Push-Button | OTE(UDT.IN.SafetyRelayResetPB) | 6
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Push-Button Input Health | OTE(UDT.IN.SafetyRelayResetPBHealth) | 7
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Output Health | OTE(UDT.IN.SafetyRelayResetHealth) | 8
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Zone ID$N | MOV(ZoneID,UDT.VAL.ZoneID) | 9
RCOMMENT | CM_SZONE_V3:AOI | Logic | TIMER PRESETS$N | DIV(UDT.WRK.tmrSafetyRelayReset.PRE,1000,UDT.CFG.SafetyRelayResetTime) | 10
RCOMMENT | CM_SZONE_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 11
RCOMMENT | CM_SZONE_V3:AOI | Logic | WORK: Evaluate Simulation State$N | OTU(UDT.LNK.SIM) | 12
RCOMMENT | CM_SZONE_V3:AOI | Logic | ZONE LINK: Fault Reset Holding Actions$N | OTE(UDT.LNK.FaultReset) | 16
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Safety Interlock Is OK$N | OTE(STS_InterlockOK) | 18
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 21
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Clear Fault Code Register If No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 22
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WHR_V3:AOI | Logic | Redundent Valve AOI Will Not Operatate As $QDouble Acting$Q, The design does not include provisions to treat a redundent valve as double acting which would require four solenoids. | OTU(UDT.CFG.DoubleSolenoid) | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WH_V3:AOI | Logic | Auto Config Switch On First Scan$N(Pre Scan Equivalent)$N | OTU(UDT.CFG.AutoHOAInService) | 2
RCOMMENT | CM_V2WH_V3:AOI | Logic | Move AOI Inputs To Correct Registers$N | OTE(UDT.IN.HandHOA) | 3
RCOMMENT | CM_V2WH_V3:AOI | Logic | Set Current HOA Mode$N | OTE(UDT.STS.HandHOAMode) | 4
RCOMMENT | CM_V2WH_V3:AOI | Logic | Set Auto Command In Manual Fault To Warning and Clear When Not Active$N | OTU(UDT.FLT.AutoCMDWhileInMan) | 6
RCOMMENT | CM_V2WH_V3:AOI | Logic | Issue Appropriate Command For Valve Configuration$N | OTU(UDT.CMD.ManualClose) | 8
RCOMMENT | CM_V2WH_V3:AOI | Logic | Monitor Input Health of HOA Switch$N | OTE(CM_V2W_V3_AOI.IN_CLSHealth) | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WR_V3:AOI | Logic | Redundent Valve AOI Will Not Operatate As $QDouble Acting$Q, The design does not include provisions to treat a redundent valve as double acting which would require four solenoids. | OTU(UDT.CFG.DoubleSolenoid) | 3
RCOMMENT | CM_V2WR_V3:AOI | Logic | FAULTS | TON(RedundentCheckCustomFaultsTMR,?,?) | 22
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V2W_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 11
RCOMMENT | CM_V2W_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosePos) | 12
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrCloseDelay.PRE,1000,UDT.CFG.CloseDelayTime) | 16
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V2W_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V2W_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 31
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 32
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Fault Reset | OTU(ExternalFault) | 35
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToClose,0.5,UDT.VAL.TimeToClose) | 38
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 39
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 40
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 43
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.WRK.bWorkingEngValve) | 47
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 48
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 52
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 65
RCOMMENT | CM_V2W_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 66
RCOMMENT | CM_V2W_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 68
RCOMMENT | CM_V2W_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 69
RCOMMENT | CM_V2W_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 70
RCOMMENT | CM_V2W_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 71
RCOMMENT | CM_V2W_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 72
RCOMMENT | CM_V2W_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 73
RCOMMENT | CM_V2W_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 74
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 4
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 5
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V3D_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InToBPos) | 6
RCOMMENT | CM_V3D_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InToAPos) | 7
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrToADelay.PRE,1000,UDT.CFG.ToADelayTime) | 16
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V3D_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V3D_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingToBValve) | 31
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingToBValve) | 32
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 35
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToB,0.5,UDT.VAL.TimeToB) | 38
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToA,0.5,UDT.VAL.TimeToA) | 39
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingToBValve) | 46
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V3D_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_V3D_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_V3D_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_V3D_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_V3D_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_V3D_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 71
RCOMMENT | CM_V3D_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 72
RCOMMENT | CM_V3D_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 4
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 5
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V3W_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InDivertPos) | 11
RCOMMENT | CM_V3W_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InStraightPos) | 12
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrStraightDelay.PRE,1000,UDT.CFG.StraightDelayTime) | 16
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V3W_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V3W_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingDivertValve) | 31
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingDivertValve) | 32
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 35
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToDivert,0.5,UDT.VAL.TimeToDivert) | 38
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToStraight,0.5,UDT.VAL.TimeToStraight) | 39
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingDivertValve) | 46
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V3W_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_V3W_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_V3W_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_V3W_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_V3W_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_V3W_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 71
RCOMMENT | CM_V3W_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 72
RCOMMENT | CM_V3W_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 6
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Close Status | OTE(UDT.STS.InClosePos) | 7
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Dribble Status | OTE(UDT.STS.InDribblePos) | 8
RCOMMENT | CM_VDB_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrDribbleDelay.PRE,1000,UDT.CFG.DribbleDelayTime) | 18
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 25
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 26
RCOMMENT | CM_VDB_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 31
RCOMMENT | CM_VDB_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 32
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(UDT.WRK.ReqDribble) | 34
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 35
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 36
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 37
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 38
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 39
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bFeedbackLS) | 40
RCOMMENT | CM_VDB_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 41
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 42
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 43
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 46
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 47
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 48
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 52
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 61
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 62
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 63
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 64
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 65
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 66
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 7 MANUAL DRIBBLE | MOV(7,UDT.VAL.HMIState) | 67
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 8 AUTO DRIBBLE | MOV(8,UDT.VAL.HMIState) | 68
RCOMMENT | CM_VDB_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 69
RCOMMENT | CM_VDB_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 71
RCOMMENT | CM_VDB_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 72
RCOMMENT | CM_VDB_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 73
RCOMMENT | CM_VDB_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 74
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Open) | 76
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Dribble) | 77
RCOMMENT | CM_VDB_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 78
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 4
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 8
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 9
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 10
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(UDT.CFG.HighSpeedSet,UDT.SET.ManualCV) | 24
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 26
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 31
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 32
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 33
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 34
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 35
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 36
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_VFD.Stop) | 4
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 34
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 39
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 40
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 41
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 42
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | OUTPUT: Setpoint | MUL(UDT.OUT.Reference,60,OUT_VFD.FreqCommand) | 44
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 45
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 46
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 4
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD755_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFD755_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFD755_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 32
RCOMMENT | CM_VFD755_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 37
RCOMMENT | CM_VFD755_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 38
RCOMMENT | CM_VFD755_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 39
RCOMMENT | CM_VFD755_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 40
RCOMMENT | CM_VFD755_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 43
RCOMMENT | CM_VFD755_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.OUT.Reference,UDT.SET.ManualCV) | 4
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDANA_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFDANA_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 8
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 9
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 10
RCOMMENT | CM_VFDANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 24
RCOMMENT | CM_VFDANA_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 30
RCOMMENT | CM_VFDANA_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 31
RCOMMENT | CM_VFDANA_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 32
RCOMMENT | CM_VFDANA_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.OUT.Reference,UDT.SET.ManualCV) | 36
RCOMMENT | CM_VFDANA_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 37
RCOMMENT | CM_VFDANA_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 38
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 1
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Command.6) | 3
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 5
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CM Routine Name: CM_PF70_5_AOI$N$NDescription: PowerFlex 70 Firmware 5.1$N$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VFDCH_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFDCH_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 20
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 21
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 22
RCOMMENT | CM_VFDCH_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 38
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 44
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 45
RCOMMENT | CM_VFDCH_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 46
RCOMMENT | CM_VFDCH_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 47
RCOMMENT | CM_VFDCH_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 49
RCOMMENT | CM_VFDCH_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 50
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 4
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 5
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 11
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 12
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 13
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | Sim Logic Changed From the AFI branch to the new$Nbranch. | CPT(UDT.VAL.RPM,(UDT.VAL.ActualSpeed/100) * UDT.VAL.RefMax) | 30
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 32
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 37
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 38
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 39
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 40
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 43
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 24
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 25
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 26
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 27
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 28
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 29
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 30
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 31
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 32
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(SpeedValidate,PIDLoop.SO) | 33
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | CLR(UDT.VAL.SpeedSP) | 34
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.Flowrate,PIDLoop.SP) | 35
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundDown) | 36
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 37
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundDown) | 38
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS$NControl Action | OTL(PIDLoop.CA) | 39
RCOMMENT | CM_VFD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(InUseResltCntrl) | 48
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.INOUT.bWorkingRunCmd) | 49
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 50
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS/OUTPUT: ENABLE VFD$N | OTE(UDT.STS.VFDEnabled) | 51
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS/OUTPUT: MANUAL ENABLE$N | OTE(UDT.STS.ManualEnabled) | 52
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: START COMMAND TO VFD | OTL(UDT.INOUT.ReqRunHold) | 53
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: STOP COMMAND TO VFD | OTU(UDT.INOUT.ReqRunHold) | 54
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 58
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 59
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND: Fault Reset | OTE(UDT.OUT.ResetFault) | 60
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Drive Fault | OTL(UDT.FLT.DriveFault) | 61
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 62
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Disconnect | OTE(UDT.STS.DisconnectActive) | 63
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Disconnect | OTL(UDT.FLT.DisconnectFault) | 64
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Input Card/Channel Faulted$N | OTL(UDT.FLT.InputCard) | 65
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Output Card/Channel Faulted$N | OTL(UDT.FLT.OutputCard) | 66
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Illegal Feedback | OTL(UDT.FLT.IllegalFeedback) | 67
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Failed To Run | OTL(UDT.FLT.FailedToStop) | 68
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 69
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 76
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 77
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Stopped | OTE(UDT.STS.AtReference) | 81
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Ready | OTE(UDT.STS.Ready) | 82
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Running | OTE(UDT.STS.Active) | 83
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Accelerating | OTE(UDT.STS.Accelerating) | 84
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Decelerating | OTE(UDT.STS.Decelerating) | 85
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Alarmed | OTE(UDT.STS.DriveAlarm) | 86
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(PIDLoop.OUT,UDT.VAL.SpeedSP) | 93
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(PIDLoop.OUT,UDT.VAL.SpeedSP) | 94
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(0,UDT.VAL.SpeedSP) | 95
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 96
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(2,UDT.VAL.HMIState) | 97
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 98
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 99
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 100
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 101
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(PIDLoop.OUT,OUT_Ref) | 102
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_Ref) | 104
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 4
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 5
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 8
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosedPos) | 9
RCOMMENT | CM_VPRANA_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 26
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 27
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 28
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 29
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 30
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 31
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 32
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 33
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 34
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SO) | 35
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 36
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 37
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SP) | 38
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 39
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 40
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 41
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS$NControl Action | OTU(PIDLoop.CA) | 42
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrClosedDelay.PRE,1000,UDT.CFG.ClosedDelayTime) | 46
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 53
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 54
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 59
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 60
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 61
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 62
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 63
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 64
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 65
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 66
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 67
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 68
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 69
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 72
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingOpenValve) | 74
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 75
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 79
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 87
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 88
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 89
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 90
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 91
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 92
RCOMMENT | CM_VPRANA_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 93
RCOMMENT | CM_VPRANA_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 95
RCOMMENT | CM_VPRANA_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 96
RCOMMENT | CM_VPRANA_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 97
RCOMMENT | CM_VPRANA_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 98
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 99
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | CPT(OUT_CV,PIDLoop.MINCV+((UDT.OUT.CV-0)/(100-0)*(PIDLoop.MAXCV-PIDLoop.MINCV))) | 100
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 101
RCOMMENT | CM_VPRANA_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 103
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 4
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 5
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 12
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosedPos) | 13
RCOMMENT | CM_VPR_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 41
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 42
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 43
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 44
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 45
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 46
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 47
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 48
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 49
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SO) | 50
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 51
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 52
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SP) | 53
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 54
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 55
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 56
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS$NControl Action | OTL(PIDLoop.CA) | 57
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrClosedDelay.PRE,1000,UDT.CFG.ClosedDelayTime) | 62
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 69
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 70
RCOMMENT | CM_VPR_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 75
RCOMMENT | CM_VPR_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 76
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 77
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 78
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 79
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 80
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AnalogInputHiAlm) | 81
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 82
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 83
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 84
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 85
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 88
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingOpenValve) | 90
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 91
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 95
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 103
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 104
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 105
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 106
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 107
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 108
RCOMMENT | CM_VPR_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 109
RCOMMENT | CM_VPR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 111
RCOMMENT | CM_VPR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 112
RCOMMENT | CM_VPR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 113
RCOMMENT | CM_VPR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 114
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 115
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | CPT(OUT_CV,PIDLoop.MINCV+((UDT.OUT.CV-0)/(100-0)*(PIDLoop.MAXCV-PIDLoop.MINCV))) | 116
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 117
RCOMMENT | CM_VPR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 120
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 4
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 5
RCOMMENT | CM_VSL_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 12
RCOMMENT | CM_VSL_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosePos) | 13
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrCloseDelay.PRE,1000,UDT.CFG.CloseDelayTime) | 17
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 25
RCOMMENT | CM_VSL_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_VSL_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 31
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 32
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 33
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 34
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 35
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 36
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 37
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 38
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToClose,0.5,UDT.VAL.TimeToClose) | 39
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.WRK.bWorkingEngValve) | 46
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_VSL_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_VSL_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_VSL_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_VSL_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_VSL_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_VSL_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 71
RCOMMENT | CM_VSL_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 72
RCOMMENT | CM_VSL_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WSGE_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_WSGE_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_WSGE_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_WSGE_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 18
RCOMMENT | CM_WSGE_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 24
RCOMMENT | CM_WSGE_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 25
RCOMMENT | CM_WSGE_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 26
RCOMMENT | CM_WSGE_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_LocalInterlock) | 27
RCOMMENT | CM_WSGE_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 28
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_WSP_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_WSP_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_WSP_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_WSP_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_WSP_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 17
RCOMMENT | CM_WSP_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 18
RCOMMENT | CM_WSP_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 19
RCOMMENT | CM_WSP_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 20
RCOMMENT | CM_WSP_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 21
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WS_V3:AOI | Logic | CONNECTIONS | MOV(IN_RawWeight,UDT.IN.RawWeight) | 0
RCOMMENT | CM_WS_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 2
RCOMMENT | CM_WS_V3:AOI | Logic | TIMER PRESETS | MOV(30,UDT.CFG.SIMWeighTime) | 5
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Control Module Fault | RES(AutoResltCntrl) | 11
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Control Module Fault | RES(AutoResltCntrl) | 12
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: In Use | OTL(UDT.STS.InUse) | 15
RCOMMENT | CM_WS_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 17
RCOMMENT | CM_WS_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 18
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 19
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Auto Gain/Loss | OTL(UDT.INOUT.bLossWeight) | 20
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Start/Stop Gain In Weight STATUS: Weigh Up In Progress STATUS: Gain In Weight Active | OTU(UDT.STS.StabComplete) | 22
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Start/Stop Loss In Weight STATUS: Weigh Up In Progress STATUS: Loss In Weight Active | OTU(UDT.STS.StabComplete) | 23
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Auto/Manual Zero | MOV(UDT.SET.Preact,UDT.VAL.Preact) | 24
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Settle | MOV(UDT.SET.SIM,UDT.VAL.TareWeight) | 25
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Stop | OTL(UDT.STS.Stopping) | 26
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Stabilize | OTU(UDT.STS.Stopping) | 27
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmEnabled) | 28
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Gain in Weight Weigh Up Complete ACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 29
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Loss in Weight Weigh Up Complete ACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 30
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Zero Deadband Status | OTE(UDT.STS.Zeroed) | 31
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Tare Weight Reading | SUB(UDT.VAL.ActualWeight,UDT.VAL.TareWeight,UDT.VAL.NetWeight) | 32
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Gain In Weight Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.NetWeight,UDT.VAL.AmountRemain) | 33
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Loss In Weight Amount Remaining | ADD(UDT.VAL.Setpoint,UDT.VAL.NetWeight,UDT.VAL.AmountRemain) | 34
RCOMMENT | CM_WS_V3:AOI | Logic | UDT.IN.SIMULATION TIMER | CPT(UDT.VAL.ActualWeight,UDT.IN.RawWeight/(UDT.CFG.RawUnitsHi-UDT.CFG.RawUnitsLo)*(UDT.CFG.EngUnitsHi-UDT.CFG.EngUnitsLo)) | 35
RCOMMENT | CM_WS_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.VAL.ActualWeight,rTotalPreviousScan) | 36
RCOMMENT | CM_WS_V3:AOI | Logic | CALCULATE DELTA | OTU(FlowRateCTL.DN) | 37
RCOMMENT | CM_WS_V3:AOI | Logic | Input: Mass Flow Rate | RES(tmrFlowRateAcc) | 38
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 45
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Fault Reset | OTU(ExternalFault) | 46
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: HI/LO Fault Timer | TON(tmrLowFlow,?,?) | 47
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoFlow) | 48
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 49
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: HI Fault Timer | TON(tmrHiFaultDelay,?,?) | 50
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: LO Fault Timer | TON(tmrLoFaultDelay,?,?) | 51
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & FAULT: Hi$N | OTL(UDT.FLT.Hi) | 52
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & FAULT: Lo | OTL(UDT.FLT.Lo) | 53
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 55
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 56
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.SingleScanDelta) | 58
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Stopping) | 62
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 63
RCOMMENT | CM_WS_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 66
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 70
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 2 WARNING | MOV(2,UDT.VAL.HMIState) | 71
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL MODE | MOV(3,UDT.VAL.HMIState) | 72
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 73
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO MODE | MOV(5,UDT.VAL.HMIState) | 74
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 75
RCOMMENT | CM_WS_V3:AOI | Prescan | CALCULATE DELTA | OTL(UDT.STS.Stopping) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 47
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 48
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 49
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 60
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 61
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 67
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 70
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 71
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | Clear Registers | MOV(10,UDT.SET.NextStateNumber) | 72
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NIf Automated Top Valve, Goto 1110 to Evaluate Logic$NIf Manual Type Top Valve, Goto 11080 to Prompt Operator to Open Vavle$N$N************************************************************************************************ | MOV(11080,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NIf Automated Bottom Valve, Goto 1150 to Evaluate Logic$NIf Manual Type Bottom Valve, Goto 11090 to Prompt Operator to Open Vavle$N$N************************************************************************************************ | MOV(11090,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$NAutomated Top Inlet Valve Logic$N$N************************************************************************************************ | MOV(11081,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$NAutomated Bottom Inlet Valve Logic$N$N************************************************************************************************ | OTE(BotInletValve.CMD.AutoOpen[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 85
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 87
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NClear the Container that was Added to the Add Pot Then goto Complete$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 88
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Destination$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 107
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate Destination Scan$N11120 = Wrong Destination Scanned$N11055 = Matching Destination$N**************************************************************************************************** | CLR(UDT.PMT.PromptType) | 108
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Intermediate Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 109
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate Intermediate Container Scan$NCopy Scan Value to Val.Cont$N$N**************************************************************************************************** | MOV(11060,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Matches$N11065 = If BatchID and Destination Match, Search For RM$N11121 = Container Match but Mismatch BatchID$N11122 = Container Match but Mismatch Destination$N**************************************************************************************************** | MOV(11122,UDT.SET.NextStateNumber) | 111
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Not Found, Add one to the Index$N$N11123 = Container Not Found$N**************************************************************************************************** | JMP(ContSearch) | 112
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Raw Material Is Found In Container$N1080 = Evaluate the Add Pot Top Type, If Manual goto 11080, If Automated goto 1110$N11124 = Raw Material Match but Wrong Item Number$N**************************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$N11125 = RM Not Found$N$N**************************************************************************************************** | JMP(RMSearch) | 114
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NManual Type Top Inlet Valve$N$NPrompt Operator to Open Top Inlet Valve and Acknolwedge When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 115
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NAutomated Type Top Inlet Valve$N$NPrompt Operator to Charge RM and Acknolwedge When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 117
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NManual Type Bottom Inlet Valve$N$NPrompt Operator to Open Bottom Inlet Valve and Acknolwedge When Complete$N$N1200 = Move Values to VAL$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 119
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 121
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 123
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 125
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Not Found$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 127
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Item Number Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 129
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container RM Not In Container$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 131
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 134
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 137
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 8
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 15
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 16
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 17
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 26
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 55
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 56
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 76
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 77
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 83
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 87
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 89
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | CLR(UDT.SET.MixTime) | 123
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | OTE(UDT.STS.InSetpointSpeed) | 144
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 172
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 8
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 15
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 16
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 17
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 26
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 55
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 56
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 76
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 77
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 83
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.MyTankNumber,UDT.VAL.MyTankNumber) | 87
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 89
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Running$N1000-4999 | CLR(UDT.SET.MixTime) | 124
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 178
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CoFeed_V2W_V2W_V3:AOI | Logic | Set In Service Bits | OTE(UDT.WRK.Delivery_A_ValveInService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CoFeed_V2W_V2W_V4:AOI | Logic | Set In Service Bits | OTE(UDT.WRK.Delivery_A_ValveInService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | 51= $QReady to Charge Material $Q$N52= $Q To $Q$N53= $Q. Scan Material Int. Container.$Q$NMessage1= $QReady to Charge Material XXX To YYY. Scan Material Int. Container.$Q | MOV(11050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NLoop Through Scale to Find Matching Scanned Scale to get ScaleIndex$N$N11128 = If Not Found Prompt Operator$N11050 = Prompt Operator if they are Ready To Start$N$N************************************************************************************************ | MOV(11068,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf the Container has Multiple RM$'s in it then Remove the RM that was Required, $Nand Mark the Container as Being Added.$N$N11095 = Prompt For Next Container or Finished Prompt$N$N************************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NVerify No Other Containers Match BatchID, ItemNo, RM$N$N****************************************************************************************************** | MOV(11106,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************************************************$N$NSearch For a Matching Container$N$N11060 = Match Found$N11121 = Found but Batch ID Mismatch$N$N****************************************************************************************************************************************** | MOV(11121,UDT.SET.NextStateNumber) | 114
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****$NIf ContIndex Goes Above 50, Go to Error $QInt. Container Not Found$Q$N11120$N$N***** | MOV(11120,UDT.SET.NextStateNumber) | 115
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************************************************$N$NSearch For Material in Scaned Container$N$N****************************************************************************************************************************************** | SUB(RM_Size,1,RM_Offset) | 116
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NIf Raw Material Is Found In Container$N11065 = Scan Destination Container$N11124 = Raw Material Match but Wrong Item Number$N**************************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 117
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$N11122 = RM Not Found$N$N**************************************************************************************************** | MOV(11122,UDT.SET.NextStateNumber) | 118
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************$N$NFound the Container and RM in the Container and everything Matches. $NNow Scan Vessel to verify Match$N$N11070 = Once Destination is Scanned Prompt to Scan Destination When Complete$N$NIf Container has Already Been Added to Vessel, Then Move to Clear Container$N11080$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 119
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************$N$NPrompt Operator if they Want to Reweigh the Intermediate Containers. The Selection$Non First Pass, it will stay until EM Completes$N$N11067 - Prompt Operator to Scan Scale For Reweigh$N$N11070 = Once Destination is Scanned Prompt to Scan Destination When Complete$N$N**************************************************************************************************** | MOV(2,UDT.PMT.PromptType) | 120
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 124
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11069 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.PromptRealEntry) | 125
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$NReweigh $N$NPrompt Operator to Place Container On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 126
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$NScan Destination Vessel/PreMix$NIf Match$N11075 = Prompt For Second Scan for Complete$NIf Doesnt Match$N11123 = Wrong Destination Scanned$N$N************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 128
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NPrompt to Scan When Complete, When Scan is Completed move to final Values$NTo VAL locations$N$N************************************************************************************************** | MOV(11085,UDT.SET.NextStateNumber) | 130
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf not a Multiple RM Container, then Clear Data From Container to allow it to be Used$Nfor another Addition. If it is a Multiple RM, then go to 11058 to Remove that Element. If it $Nis a Multiple RM and It has already been marked as Added, then Clear Data.$N$N1090 = Remove Added RM from Container, Mark As Added$N11095 = Prompt For Next Container or Finished$N$N************************************************************************************************** | MOV(1090,UDT.SET.NextStateNumber) | 131
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NCreate String Entry Prompt For Operator to Select $QNext Container$Q or $QFinished$Q$NThen Move to 11100 to Process the Selection$N$N************************************************************************************************** | MOV(11100,UDT.SET.NextStateNumber) | 132
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf $QNext Container$Q Selected Move to 1050 To Start Over Again$N$NIf $QFinished$Q Selected Move to 11105 to Finish $N$N************************************************************************************************** | MOV(0,UDT.PMT.PromptType) | 133
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NSearch Through Containers to Find a Matching BatchID.$N11107 = If Found Matching BatchID - Look at RM & ItemNo$N11110 = Clean Up No Other Containers Match$N$N****************************************************************************************************** | MOV(11107,UDT.SET.NextStateNumber) | 134
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NSearch Through Raw Materials of Container to Find a Matching Item Number and RM Code$N11108 = If Found Matching ItemNo and RM_Code, Prompt Operator if they are Finished$N11110 = Clean Up No Other Containers Match$N$N****************************************************************************************************** | MOV(11108,UDT.SET.NextStateNumber) | 136
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NFinish any Clean up then Go Complete$N9500$N$N****************************************************************************************************** | MOV(9500,UDT.SET.NextStateNumber) | 139
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NIf No Container Is Found Prompt$NOperator $N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 140
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NIf Container Found But Wrong BatchID Prompt$NOperator $N$N1050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 142
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$N Raw Material Is Not Found in Container Prompt$NOperator $N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 144
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *******************************************************************************************************$N$NWrong Destination Barcode Scanned$NPrompt Operator of Error, Then Prompt to Scan$N$N11065 = Scan Destination Vessel/PreMix$N$N*********************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 146
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *******************************************************************************************************$N$NCorrect Raw Material but Wrong Item Number In Container$NPrompt Operator of Error, Then Prompt to Scan Another Container$N$N1050 = Scan Destination Vessel/PreMix$N$N*********************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 148
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 150
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 154
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 157
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 0
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.FLT.Custom.0) | 17
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | This routine executes the following generic paint logic :$NWW Density Alarming, Solids Calculations, Required Yield Var Hit, Rework Hit | OTE(UDT.STS.GP.WWInitialFlushComplete) | 24
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | WW Vol GP = (( WW Density - 8.31) / 2.34 ) * WW Vol Deliv$NWhere : $T$NWW Density = Totalized WW Mass Delivered / Totalized WW Volume Delivered$N8.31 = Density of Water$N2.34 = 10.65 - 8.31 (Assumed Density of Paint - Density of Water)$NWW Vol Deliv = Totalized WW Volume Delivered | CPT(UDT.VAL.GP.GP_Volume_Actual,(UDT.VAL.GP.WW_Density-UDT.SET.GP.Water_Density)/(UDT.SET.GP.WW_Density-UDT.SET.GP.Water_Density)*UDT.VAL.GP.Volume_Actual) | 29
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | MOV(0,UDT.VAL.GP.WWDoneReason) | 30
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.STS.GP.WWDone) | 31
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Yield Var Hit (lbs) = Volume of GP Added * 8.31 (Density of Water) | MUL(UDT.VAL.GP.GP_Volume_Actual,UDT.SET.GP.WW_Density,UDT.VAL.GP.GP_Mass_Actual) | 32
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Rework Volume Hit = GP max Volume - Volume of GP delivered | CLR(UDT.VAL.GP.RW_Volume_Setpoint) | 36
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 0
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.FLT.Custom.0) | 13
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | This routine executes the following generic paint logic :$NWW Density Alarming, Solids Calculations, Required Yield Var Hit, Rework Hit | OTE(UDT.STS.GP.WWInitialFlushComplete) | 20
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | WW Vol GP = (( WW Density - 8.31) / 2.34 ) * WW Vol Deliv$NWhere : $T$NWW Density = Totalized WW Mass Delivered / Totalized WW Volume Delivered$N8.31 = Density of Water$N2.34 = 10.65 - 8.31 (Assumed Density of Paint - Density of Water)$NWW Vol Deliv = Totalized WW Volume Delivered | CPT(UDT.VAL.GP.GP_Volume_Actual,(UDT.VAL.GP.WW_Density-UDT.SET.GP.Water_Density)/(UDT.SET.GP.WW_Density-UDT.SET.GP.Water_Density)*UDT.VAL.GP.Volume_Actual) | 25
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | MOV(0,UDT.VAL.GP.WWDoneReason) | 26
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.STS.GP.WWDone) | 27
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Yield Var Hit (lbs) = Volume of GP Added * 8.31 (Density of Water) | MUL(UDT.VAL.GP.GP_Volume_Actual,UDT.SET.GP.WW_Density,UDT.VAL.GP.GP_Mass_Actual) | 28
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Rework Volume Hit = GP max Volume - Volume of GP delivered | CLR(UDT.VAL.GP.RW_Volume_Setpoint) | 32
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 85
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | MOV(11050,UDT.SET.NextStateNumber) | 88
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NIf Preweigh is a Bulk Storage Type goto 11075, Otherwise goto 11060$N11075 will utilize Valves and Pumps From Bulk Storage to Scale$N11060 will utilize Operator Additions to a Container on the Scale$N$N************************************************************************************************ | MOV(11060,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NAfter Scanning in Container and Raw Material Information Store Information$Nin the Container User Defined Structure$N$NOnce Stored Continue on with Logic to have Operator Setup the Scale 11085$N$N********************************************************************************************** | MOV(1090,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(1120,UDT.SET.NextStateNumber) | 93
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 101
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.TOLERANCE,EM_DLY[DLYIndex].SET.TolerancePCT) | 108
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint | MOV(11100,UDT.SET.NextStateNumber) | 109
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N************************************************************************************************ | MOV(UDT.WRK.UserBit,SCALE[ScaleIndex].VAL.InUseBy[0]) | 110
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N************************************************************************************************ | MOV(UDT.WRK.UserBit,SCALE[ScaleIndex].VAL.InUseBy[0]) | 111
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1200,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 114
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 115
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 134
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 135
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 136
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 137
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 138
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$N11060 = Batch IDs Match Continue Logic$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | MOV(0,UDT.PMT.PromptType) | 139
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11065 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 140
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 142
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Intermediate Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 144
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Matches$N1080 = Container Is Empty$N11080 = Container has BatchID, Prompt to Use Same Container$N11126 = Container Match but Mismatch BatchID$N11125 = Container Match but Mismatch Destination$N**************************************************************************************************** | MOV(11126,UDT.SET.NextStateNumber) | 146
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Not Found, Add one to the Index$N$N11123 = Container Not Found$N**************************************************************************************************** | JMP(ContSearch) | 147
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator Container Already Being Used, Want to Add To It?$N11081 - Add to the Container that has Something in it$N11075 - Rescan Intermediate Container$N$N************************************************************************************************** | MOV(2,UDT.PMT.PromptType) | 148
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | 1=Yes$N2=No | CLR(UDT.PMT.Message2.LEN) | 149
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NSearch For RM in Container that is not Empty. $NLook for the same RM_Code to add to that element$NIf same RM_Code is not in there then add to the Container in the next Open $NElement. Also mark Container and MultiRM.$NIf a RM_Code is Matched and the ItemNo is different set error to Scan another container$N**************************************************************************************************** | MOV(11127,UDT.SET.NextStateNumber) | 150
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$NIf neither a blank or matching RM_Code exists then set a gnernal Error to$NScan another Continer$N11123 = Container Error$N$N**************************************************************************************************** | JMP(RMSearch) | 151
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11100 - Prompt For Next Cont. or Finished$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 153
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Not Found$N11075 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NDestinatino Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof Destination$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof BatchID$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof ItemNumber$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 185
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 188
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 81
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | OTU(UDT.WRK.ChangeScale) | 87
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NAfter the Operators Places the Empty Pallet On the Scale and Scans$NGet weight, Subtract the Final Weight From the Initial Weight to Get the Charged$NWeight.$NIf this is the First RM Charge/Lot Number, then place it in VAL.Cont[0].$NIf this is the >0 charge check to see if the current charge has the same Lot/RM as$Nthe Previous. If it is the same then add to it if not add it ot the next Open Cont.$N$N$N********************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(11094,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 100
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.Mode,EM_DLY[DLYIndex].SET.Mode) | 107
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint$N$NAFI on second branch, was added to allow tracking of the actual during a delivery and not just totalize$Nthe value at the end of a delivery. The rung above it is where the calculation is being done now. | MOV(11096,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N11105 - Over Weight Tolerance, Ask For Reweigh or Supervisors Approval$N11065 - Weight Within Tolerance, Prompt Operator to Scan Raw Materail$N$NReAquire Scale $N$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 111
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N11106 - Over Weight Tolerance, Prompt Operator For Reweigh or Supervisors Approval$N11105 - Under Weight Tolerance, Ask if they Want to add Another Container or Continue with Supervisors Approval$N1200 - Weight In Tolerance, Continue to Cleanup$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 112
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1194,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 121
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 122
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 141
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 142
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 143
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 144
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 145
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$NIf a Manual Charge, that means there has to be a Hatch and a barcode to scan for the $Ndestination. If it is an auto charge, then we dont have to scan the destination barcode.$N11060 = Batch IDs Match Continue Logic - Scan Destination$N11065 - Batch IDs Match but Auto Charge - RM Code$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 146
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NScan Destination Location$N11065 - Scan Material Code$N11125 - Destination Not Found$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 147
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11070 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 149
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 152
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11080 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 155
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Charge Material X to Vessel Y and Scan Hatch When Complete$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet Back On Scale and Scan Get Weight$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(1141,UDT.SET.NextStateNumber) | 169
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Blow Down Line, Confirm When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Confirms Line Is Blown Down.$N**************************************************************************************************** | MOV(1196,UDT.SET.NextStateNumber) | 171
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11060 = Scan Destination$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 184
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 186
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 188
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 191
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 194
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 81
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | OTU(UDT.WRK.ChangeScale) | 87
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NAfter the Operators Places the Empty Pallet On the Scale and Scans$NGet weight, Subtract the Final Weight From the Initial Weight to Get the Charged$NWeight.$NIf this is the First RM Charge/Lot Number, then place it in VAL.Cont[0].$NIf this is the >0 charge check to see if the current charge has the same Lot/RM as$Nthe Previous. If it is the same then add to it if not add it ot the next Open Cont.$N$N$N********************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(11094,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 100
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.Mode,EM_DLY[DLYIndex].SET.Mode) | 107
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint$N$NAFI on second branch, was added to allow tracking of the actual during a delivery and not just totalize$Nthe value at the end of a delivery. The rung above it is where the calculation is being done now. | MOV(11096,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N11105 - Over Weight Tolerance, Ask For Reweigh or Supervisors Approval$N11065 - Weight Within Tolerance, Prompt Operator to Scan Raw Materail$N$NReAquire Scale $N$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 111
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N11106 - Over Weight Tolerance, Prompt Operator For Reweigh or Supervisors Approval$N11105 - Under Weight Tolerance, Ask if they Want to add Another Container or Continue with Supervisors Approval$N1200 - Weight In Tolerance, Continue to Cleanup$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 112
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1194,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 121
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 122
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 141
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 142
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 143
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 144
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 145
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$NIf a Manual Charge, that means there has to be a Hatch and a barcode to scan for the $Ndestination. If it is an auto charge, then we dont have to scan the destination barcode.$N11060 = Batch IDs Match Continue Logic - Scan Destination$N11065 - Batch IDs Match but Auto Charge - RM Code$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 146
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NScan Destination Location$N11065 - Scan Material Code$N11125 - Destination Not Found$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 147
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11070 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 149
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 152
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11080 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 155
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Charge Material X to Vessel Y and Scan Hatch When Complete$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet Back On Scale and Scan Get Weight$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(1141,UDT.SET.NextStateNumber) | 169
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Blow Down Line, Confirm When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Confirms Line Is Blown Down.$N**************************************************************************************************** | MOV(1196,UDT.SET.NextStateNumber) | 171
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11060 = Scan Destination$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 184
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 186
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 188
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 191
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 194
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_CHASE_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PURGE_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_DPH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_PMR_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V3W_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V3W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_SADD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_HOLD_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_HOLD_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_HOLD_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_HOLD_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_HOLD_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_HOLD_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_HOLD_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_HOLD_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_HOLD_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 100
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 103
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_PMPT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_PMPT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_PMPT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_PMPT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_PMPT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_PMPT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_PMPT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_PMPT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_PMPT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 112
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 115
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_QC_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_QC_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_QC_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_QC_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_QC_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_QC_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_QC_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_QC_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_QC_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_QD_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Resource Arbitration Manager$N$NThis routine will coordinate which unit currently owns a resource.$N | NOP() | 0
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 1
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,ProdLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 3
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 7
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | QUEUING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.CMD.ClearQueue) | 11
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.FSC_CONTROL_1) | 12
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | FLL(0,UDT.WRK.InUseRef[0],UDT.WRK.CMDAutoDINT) | 13
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.WRK.bLoadQueueBuffer) | 14
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Check to see if Request ID has already been loaded into the Que | MOV(UDT.WRK.QueueBuffer[0],UDT.WRK.QueueUnload) | 16
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Check to see if Request ID has already been loaded into the Que | RES(UDT.WRK.FSC_CONTROL_1) | 17
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | MOV(UDT.WRK.QueuePrioritySize,UDT.WRK.QueueUnloadControl.LEN) | 18
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | RES(UDT.WRK.QueueUnloadControl) | 19
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | MOV(UDT.WRK.QueuePrioritySize,UDT.WRK.QueueLoadControl.LEN) | 20
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | RES(UDT.WRK.QueueLoadControl) | 21
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | CLR(UDT.SET.ReqNextPathNumber) | 24
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(UDT.VAL.CurrentUser,UDT.WRK.LSCurrentUser) | 31
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 33
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | FLL(0,UDT.VAL.InUseBy[0],5) | 34
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | COMMAND: Auto Open/Close | OTL(UDT.WRK.Enable) | 41
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(IN_USE) | 64
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(IN_QUEUE) | 65
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(0,UDT.VAL.HMIState) | 66
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(2,UDT.VAL.HMIState) | 67
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(1,UDT.VAL.HMIState) | 68
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(6,UDT.VAL.HMIState) | 69
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(3,UDT.VAL.HMIState) | 70
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Chase Active | MOV(7,UDT.VAL.HMIState) | 71
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(4,UDT.VAL.HMIState) | 72
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(5,UDT.VAL.HMIState) | 73
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 74
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(ProdLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 75
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 79
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTE(UDT.FLT.InterruptsDisabled) | 80
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.UsingModuleFault) | 81
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.UsingTableFull) | 82
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 88
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1300,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1300,UDT.SET.NextStateNumber) | 93
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Hold) | 95
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTL(UDT.CMD.ClearQueue) | 102
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 105
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Current User Has Been Released / Aborted Before $NUser Had Become Confirmed User | CLR(UDT.VAL.CurrentUser) | 114
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | MOV(UDT.SEQ.CurrentStep.NextPath,UDT.SET.NextPathNumber) | 145
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.WRK.DevicesVerified) | 146
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | MUL(UDT.SEQ.CurrentStep.FaultTime,1000,UDT.WRK.FaultTimer.PRE) | 147
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | TON(UDT.WRK.FaultTimer,0,0) | 148
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(UDT.VAL.PathNumber,UDT.WRK.LSStateNumber) | 155
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 158
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[7],UDT.VAL.InUseBy[7],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[7],UDT.VAL.InUseByID[7],UDT.WRK.InUseByAOI[7].UserPriority,UDT.VAL.InUseByTypeArray[7]) | 159
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[15],UDT.VAL.InUseBy[15],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[15],UDT.VAL.InUseByID[15],UDT.WRK.InUseByAOI[15].UserPriority,UDT.VAL.InUseByTypeArray[15]) | 160
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[23],UDT.VAL.InUseBy[23],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[23],UDT.VAL.InUseByID[23],UDT.WRK.InUseByAOI[23].UserPriority,UDT.VAL.InUseByTypeArray[23]) | 161
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[31],UDT.VAL.InUseBy[31],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[31],UDT.VAL.InUseByID[31],UDT.WRK.InUseByAOI[31].UserPriority,UDT.VAL.InUseByTypeArray[31]) | 162
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(UDT.WRK.Queue[1],UDT.VAL.QueuedUsers[0],UDT.WRK.QueueSizeLessOne) | 164
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_STATUS_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_STATUS_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 11
RCOMMENT | EM_STATUS_V1:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 14
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(0,UDT.VAL.HMIState) | 19
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(2,UDT.VAL.HMIState) | 24
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(1,UDT.VAL.HMIState) | 25
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(6,UDT.VAL.HMIState) | 26
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(3,UDT.VAL.HMIState) | 27
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(4,UDT.VAL.HMIState) | 28
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(5,UDT.VAL.HMIState) | 29
RCOMMENT | EM_STATUS_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyIndex[0],UDT.VAL.UsingID[0],32) | 31
RCOMMENT | EM_STATUS_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 63
RCOMMENT | EM_STATUS_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(UDT.FLT.UsingTableFull) | 64
RCOMMENT | EM_STATUS_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 65
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPJK_V1:AOI | Logic | Safe State | NOP() | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_V1:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 7
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_V2:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 7
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 8
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EP_Ctrl_V2:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EX_REQ_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EX_REQ_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EX_REQ_V3:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 2
RCOMMENT | EX_REQ_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 10
RCOMMENT | EX_REQ_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 21
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | LibAnalog_Input:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Alarm_HIHI) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Alarm_HIHI) | 2
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Density_Alarm_HIHI) | 8
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Temp_Alarm_HIHI) | 12
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Drive_Gain_Alarm_HIHI) | 16
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** If Auto or Manual and a there is a request to open the valve and interlocks are true then Energize the valve The Interlock must be On for the device to be enabled ************************************************** | TOF(RunDlyOff,?,?) | 6
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** When the Valve is energized and the limit switches are not in the correct position then run the open timer. ************************************************** | TON(RUN_TMR,?,?) | 13
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** When the Valve is de-energized and the limit switches are not in the correct position then run the close timer. ************************************************** | TON(OFF_TMR,?,?) | 15
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore only the closed limit is used for fault position If the valve is energized open and the closed limit is still on then the valve is faulted when the timer completes Else if the valve is de-energized and the closed limit is not made then the valve is faulted when the timer completes ************************************************** | OTE(FAULT_STS) | 20
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 1 Calculation$N*************************************************** | CLR(TotalAddedCur[0]) | 32
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 2 Calculation$N*************************************************** | CLR(TotalAddedCur[1]) | 36
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 3 Calculation$N*************************************************** | CLR(TotalAddedCur[2]) | 40
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 4 Calculation$N*************************************************** | CLR(TotalAddedCur[3]) | 44
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 5 Calculation$N*************************************************** | CLR(TotalAddedCur[4]) | 48
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** If Auto or Manual and a there is a request to open the valve and interlocks are true then Energize the valve The Interlock must be On for the device to be enabled ************************************************** | TOF(CloseDly,?,?) | 6
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** When the Valve is energized and the limit switches are not in the correct position then run the open timer. ************************************************** | TON(OPEN_TMR,?,?) | 11
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** When the Valve is de-energized and the limit switches are not in the correct position then run the close timer. ************************************************** | TON(CLOSE_TMR,?,?) | 13
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore the Open limit is used to warn the operator of the possible problem If the valve is energized open and the open limit is off then the valve is in warning when the timer completes Else if the valve is de-energized and the Open limit is made then the valve is in warning when the timer completes ************************************************** | OTE(OPEN_FLT) | 16
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore only the closed limit is used for fault position If the valve is energized open and the closed limit is still on then the valve is faulted when the timer completes Else if the valve is de-energized and the closed limit is not made then the valve is faulted when the timer completes ************************************************** | OTE(CLOSE_FLT) | 17
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ***************************************************$NMeter Calculation$N*************************************************** | CLR(TotalAddedCur) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | MM_CIR_V1:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | MM_CIR_V1:AOI | Logic | Prevent RECIRC From Causing Module To Go InUse | MOV(0,locIndirectUserID[1]) | 2
RCOMMENT | MM_CIR_V1:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrTimeInRange.PRE,60000,UDT.CFG.TimeInRange) | 7
RCOMMENT | MM_CIR_V1:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 8
RCOMMENT | MM_CIR_V1:AOI | Logic | Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 9
RCOMMENT | MM_CIR_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 10
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 17
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 18
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 19
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 20
RCOMMENT | MM_CIR_V1:AOI | Logic | Reset Faults$N | OTU(UDT.FLT.SystemFaultTimeOFF) | 22
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.STS.WaitInRangeTime) | 23
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 24
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.STS.WaitInRangeTime) | 25
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 26
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 27
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 33
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 34
RCOMMENT | MM_CIR_V1:AOI | Logic | VALUE: PhaseA | CLR(UDT.VAL.PhaseC) | 37
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 43
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 44
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 5 NORMAL CONDITIONS | MOV(5,UDT.VAL.HMIState) | 45
RCOMMENT | MM_CIR_V1:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 46
RCOMMENT | MM_CIR_V1:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 47
RCOMMENT | MM_CIR_V1:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(IN_SuppressAlarms) | 48
RCOMMENT | MM_CIR_V1:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 49
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 50
RCOMMENT | MM_CIR_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 51
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_CHAR_V1:AOI | Logic | If raw rate is less than X00, set characterized value to Y00.$NJump to the end of the subroutine.$N | JMP(label_0) | 0
RCOMMENT | SM_CHAR_V1:AOI | Logic | If raw rate is greater than X10, set characterized value to Y10.$NJump to the end of the subroutine. | JMP(label_0) | 1
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X00 and less than X01, move X00 to XL,$NX01 to XG, Y00 to YL and Y01 to YG.$N | MOV(Char.Adjustment_Point[1].Output,CHR_MULT_LOW_VALUE) | 2
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X01 and less than X02, move X01 to XL,$NX02 to XG, Y01 to YL and Y02 to YG.$N | MOV(Char.Adjustment_Point[2].Output,CHR_MULT_LOW_VALUE) | 3
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X02 and less than X03, move X02 to XL,$NX03 to XG, Y02 to YL and Y03 to YG.$N | MOV(Char.Adjustment_Point[3].Output,CHR_MULT_LOW_VALUE) | 4
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X03 and less than X04, move X03 to XL,$NX04 to XG, Y03 to YL and Y04 to YG. | MOV(Char.Adjustment_Point[4].Output,CHR_MULT_LOW_VALUE) | 5
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X04 and less than X05, move X04 to XL,$NX05 to XG, Y04 to YL and Y05 to YG. | MOV(Char.Adjustment_Point[5].Output,CHR_MULT_LOW_VALUE) | 6
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X05 and less than X06, move X05 to XL,$NX06 to XG, Y05 to YL and Y06 to YG. | MOV(Char.Adjustment_Point[6].Output,CHR_MULT_LOW_VALUE) | 7
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X06 and less than X07, move X06 to XL,$NX07 to XG, Y06 to YL and Y07 to YG.$N | MOV(Char.Adjustment_Point[7].Output,CHR_MULT_LOW_VALUE) | 8
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X07 and less than X08, move X07 to XL,$NX08 to XG, Y07 to YL and Y08 to YG. | MOV(Char.Adjustment_Point[8].Output,CHR_MULT_LOW_VALUE) | 9
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X08 and less than X09, move X08 to XL,$NX09 to XG, Y08 to YL and Y09 to YG.$N | MOV(Char.Adjustment_Point[9].Output,CHR_MULT_LOW_VALUE) | 10
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X09 and less than X10, move X09 to XL,$NX10 to XG, Y09 to YL and Y10 to YG. | MOV(Char.Adjustment_Point[10].Output,CHR_MULT_LOW_VALUE) | 11
RCOMMENT | SM_CHAR_V1:AOI | Logic | Calculate the characterized flow rate using the following formula:$NCHAR RATE = (((RAW RATE - XL) / (XG - XL)) * (YG - YL)) + YL | CPT(Char.OUT_Value,(Char.IN_ComparePV-CHR_PROC_LOW_VALUE)/(CHR_PROC_HIGH_VALUE-CHR_PROC_LOW_VALUE)*(CHR_MULT_LOW_VALUE-CHR_MULT_HIGH_VALUE)+CHR_MULT_HIGH_VALUE) | 12
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_Count_V1:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 0
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | EnableInFalse | No Active Faults Exist | OTU(ExternalFault) | 1
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | No Active Faults Exist | OTU(ExternalFault) | 17
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | Condition Active Fault Latching$N | SUB(FaultBit,1,ActiveFault) | 19
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | This Is Required For Situations Where Multiple Faults Occur At The Same Time$N | CLR(FaultBit) | 20
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.VAL.UserBit,UserBitID AND 31) | 1
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | Search Through The Source Info Storage Registers for Matching Source$N | OTE(IndexEqual) | 9
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | Search Through The Source Info Storage Registers for Matching Source$N | MOV(UDT.SEQ.Path[locLoopIndex].ID,locSearchValue) | 18
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_IndirectEMAgit_V1:AOI | Logic | Clear Out Old User Info$N | CLR(EM_AGIT.SET.InUseBy[1]) | 1
RCOMMENT | SM_IndirectEMAgit_V1:AOI | Logic | Set user ID Where It Applies$N | MOV(InUseBy1,EM_AGIT.SET.InUseBy[1]) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_IndirectUsing_V3:AOI | Logic | Unlatch User From Previous Scan If It Is No Longer In Use BUT Also Verify It Hasn$'t Changed Position$N | OTU(AutoEnable[(PrevInUseBy1 AND (NOT 31))/32].[PrevInUseBy1 AND 31]) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | DISABLE INTERRUPTS FOR FOLLOWING RUNGS$N | UID() | 2
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | REMOVE DATA FROM PREVIOUS USER LIST | OTL(ER) | 3
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | REMOVE DATA FROM PREVIOUS USER LIST | CLR(UserBitID) | 4
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | DETERMINE IF ALREADY IN LIST | OTL(ER) | 7
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | ENABLE INTERRUPTS | UIE() | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NCapture the current flow rate (in lbs/sec) while the the product is batching (prior to the valve shutoff signal).$N$N**************************************************************************************************************************************$N | DIV(DLY.VAL.Flowrate,60.0,FlowLbPerSecStore) | 0
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf there is an auto addition that just completed shift and update the error samples in the FIFO.$N$N**************************************************************************************************************************************$N | OTL(UpdatePreactCalcs) | 3
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf there are 3 error samples in a row that are all positive or all negative, turn on the command to adjust the preact.$N$N**************************************************************************************************************************************$N | OTE(PreactAdjustCmd) | 5
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf the preact adjust command is on calculate the average error as the total of the last 3 samples divided by 3.$NAlso calculate the error adjustment as:$N$N Preact Error Adjust = Average Error * Preact Adjust Percent / 100.0$N$NIf the flow adjust is not enabled, add the preact error adjust to the current preact setpoint.$N$NIf the flow adjust is enabled, convert the average error from weight in pounds to time in seconds by dividing$Nby the flow rate and add this to the preact time.$N$N**************************************************************************************************************************************$N | ADD(PreactTimeSP,CalcPreactTimeAdj,PreactTimeSP) | 7
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf the preact flow adjust is enabled, calculate the preact as:$N Preact in pounds = Flow Rate in Lb/Sec * Preact Time in seconds$N$N**************************************************************************************************************************************$N | OTL(DLY.CMD.UpdatePreact) | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Initialize All Registers$N | OTU(EnableOut) | 2
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Exit If No Source From MES$N | JMP(Abort) | 3
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value$N | MOV(SourceMES,locSourcePath) | 4
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Search Through The Source Info Storage Registers for Matching SourcePath | MOV(SourceInfo.Table[LoopIndex].Source,SearchValue) | 6
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Abort If Source Not Found In SourceInfo Table$N | JMP(Abort) | 8
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Search Through SourceProp Table To Find Source$N | MOV(SourceProp.Prop[LoopIndex].SourceNo,SearchValue) | 10
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Abort If Source Not Found In SourceProp Table$N | JMP(Abort) | 12
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value After All Tables Have Been Verified$N | MOV(UDT.WRK.CapturedSourcePath,SourcePath) | 13
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value After All Tables Have Been Verified$N | MOV(UDT.WRK.CapturedTankPath,TankPath) | 14
TAG |  | JBS_Z4_021:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:4:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:4:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:5:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:5:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:6:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:6:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:7:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_021:7:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_ZA_001:1:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZA_001:1:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZA_001:2:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZA_001:2:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:3:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:3:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:4:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:4:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:5:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_061:5:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:10:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:10:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:10:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:11:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:11:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:11:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:12:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:12:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:13:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:13:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:14:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:14:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:15:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:15:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:16:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:16:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:17:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:17:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:18:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:18:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:19:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:19:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:20:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:20:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:21:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:21:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:6:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:6:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:6:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:7:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:7:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:7:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:8:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:8:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:8:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:9:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:9:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_041:9:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:1:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:1:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:2:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:2:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:3:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:3:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:4:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z4_001:4:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:10:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:10:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:10:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:11:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:11:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:11:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:12:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:12:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:13:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:13:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:14:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:14:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:15:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:15:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:16:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:16:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:17:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:17:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:18:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:18:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:19:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:19:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:20:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:20:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:21:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:21:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:6:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:6:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:6:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:7:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:7:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:7:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:8:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:8:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:8:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:9:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:9:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_001:9:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:10:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:10:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:11:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:11:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:12:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:12:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:13:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:13:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:14:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:14:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:15:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:15:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:16:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:16:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:17:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:17:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:6:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:6:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:6:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:7:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:7:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:7:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:8:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:8:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:9:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z5_001:9:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:10:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:10:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:11:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:11:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:12:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:12:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:13:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:13:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:14:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:14:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:6:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:6:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:6:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:7:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:7:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:7:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:8:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:8:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:9:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_031:9:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_MOT_001:1:C |  | AB:1756_DO:C:0 |  | (ExternalAccess := Read/Write)
ALIAS |  | JBS_MOT_001:1:I |  |  | JBS_MOT_001:I.Slot[1] | (ExternalAccess := Read/Write)
ALIAS |  | JBS_MOT_001:1:O |  |  | JBS_MOT_001:O.Slot[1] | (ExternalAccess := Read/Write)
TAG |  | JBS_MOT_001:2:C |  | AB:1756_DO:C:0 |  | (ExternalAccess := Read/Write)
ALIAS |  | JBS_MOT_001:2:I |  |  | JBS_MOT_001:I.Slot[2] | (ExternalAccess := Read/Write)
ALIAS |  | JBS_MOT_001:2:O |  |  | JBS_MOT_001:O.Slot[2] | (ExternalAccess := Read/Write)
TAG |  | JBS_MOT_001:3:C |  | AB:1756_DI:C:1 |  | (ExternalAccess := Read/Write)
ALIAS |  | JBS_MOT_001:3:I |  |  | JBS_MOT_001:I.Slot[3] | (ExternalAccess := Read/Write)
TAG |  | JBS_MOT_001:I |  | AB:1756_ENET_13SLOT:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_MOT_001:O |  | AB:1756_ENET_13SLOT:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:1:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:1:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:2:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:2:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:3:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:3:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:4:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:4:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:5:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_ZI_001:5:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:5:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:5:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:6:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:6:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:7:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:7:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:8:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:8:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:9:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z7_001:9:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:10:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:10:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:10:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:11:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:11:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:11:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:12:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:12:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:13:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:13:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:14:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:14:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:15:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:15:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:16:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:16:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:17:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:17:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:18:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:18:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:19:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:19:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:20:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:20:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:6:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:6:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:6:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:7:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:7:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:7:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:8:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:8:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:8:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:9:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:9:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_002:9:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:10:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:10:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:11:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:11:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:12:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:12:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:6:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:6:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:7:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:7:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:8:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:8:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:9:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z6_021:9:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z3_001:1:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z3_001:1:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:4:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:4:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:5:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:5:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:6:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z1_001:6:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:10:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:10:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:3:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:3:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:3:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:4:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:4:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:4:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:5:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:5:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:5:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:6:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:6:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:7:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:7:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:8:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:8:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:9:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_021:9:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:1:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:1:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:1:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:2:C |  | AB:1718_19_DO2:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:2:I |  | AB:1718_19_DO2:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:2:O |  | AB:1718_19_DO2:O:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:3:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:3:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:4:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:4:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:5:C |  | AB:1718_19_DI8:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:5:I |  | AB:1718_19_DI8:I:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:6:C |  | AB:1718_19_AI4_HART:C:0 |  | (ExternalAccess := Read/Write)
TAG |  | JBS_Z2_001:6:I |  | AB:1718_19_AI4_HART:I:0 |  | (EngineeringUnit.CH01.DATA := "%", EngineeringUnit.CH02.DATA := "%", EngineeringUnit.CH03.DATA := "%", EngineeringUnit.CH04.DATA := "%", ExternalAccess := Read/Write)
TAG |  | Active_Prompts_EID |  | STRING_20[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | ALARM_HORN |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | ALARM_HORN_ACK |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | AlwaysFalse | Always False. Constant Set to Zero. | BOOL |  | (RADIX := Decimal, Constant := true, ExternalAccess := Read Only)
ALIAS |  | BLANK_AIN |  |  | CM_AIN[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_AOD |  |  | CM_AOD[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_AOUT |  |  | CM_AOUT[0] | (ExternalAccess := Read/Write)
TAG |  | BLANK_BOOL |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | BLANK_DI |  |  | CM_DI[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_DLY |  |  | EM_DLY[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_DOUT |  |  | CM_DOUT[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_IND560 |  |  | CM_IND560[0] | (ExternalAccess := Read/Write)
TAG |  | BLANK_IND570 |  | uCM_WS_V3 |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | BLANK_M2S |  |  | CM_M2S[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_MDG |  |  | CM_MDG[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_MET |  |  | CM_MP4[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_MM_CIR |  |  | MM_CIR[0] | (ExternalAccess := Read Only)
ALIAS |  | BLANK_MP4 |  |  | CM_MP4[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_MPG |  |  | CM_MPG[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_pc_V2W |  |  | pc_V2W_Array[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_PMR |  |  | CM_PMR[0] | (ExternalAccess := Read/Write)
TAG |  | Blank_Real |  | REAL |  | (RADIX := Float, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | BLANK_RECIRC |  |  | EM_RECIRC[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_RM | Resource Manager For NK_RM |  | EM_RSC_MGR[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_SF |  |  | CM_SF[0] | (ExternalAccess := Read/Write)
TAG |  | BLANK_STRING |  | STRING |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | BLANK_STRING_20 |  | STRING_20 |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | BLANK_SZ |  |  | CM_SZONE[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_V2W |  |  | CM_V2W[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_V2WHR |  |  | CM_V2WHR[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_V2WR |  |  | CM_V2WR[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_V3D |  |  | CM_V3D[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_V3W |  |  | CM_V3W[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VDB |  |  | CM_VDB[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VFD2S |  |  | CM_VFD2S[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VFD755 |  |  | CM_VFD755[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VFDCH |  |  | CM_VFDCH[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VPR |  |  | CM_VPR[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_VSL |  |  | CM_VFDCH[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_WS |  |  | CM_WSP[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_WSGE |  |  | CM_WSGE[0] | (ExternalAccess := Read/Write)
ALIAS |  | BLANK_WSP |  |  | CM_WSP[0] | (ExternalAccess := Read/Write)
TAG |  | Clx_Status |  | udsControllerDevice |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CLx_SysStatus |  | udsSysStatus |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_AIN |  | uCM_AIN_V3[500] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_AOD |  | uCM_AOD_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_AOUT |  | uCM_AOUT_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_DI |  | uCM_DIN_V5[300] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_DIFF |  | uCM_DIFF_V3[10] |  | (Constant := false, ExternalAccess := Read Only)
TAG |  | CM_DOUT |  | uCM_DOUT_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_IND560 |  | uCM_WS_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_M2S |  | uCM_M2S_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_MDG |  | uCM_MET_V3[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_MP4 |  | uCM_MET_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_MPG |  | uCM_MET_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_PMR |  | uCM_PMR_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_SF |  | uCM_SF_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_SZONE |  | uCM_ZON_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_SZ_EMModules |  | CM_SZONE_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_SZ_SystemWide |  | CM_SZONE_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_V2W |  | uCM_V2W_V3[500] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_V2WHR |  | uCM_V2W_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_V2WR |  | uCM_V2W_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_V3D |  | uCM_V3D_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_V3W |  | uCM_V3W_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VDB |  | uCM_VDB_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VFD2S |  | uCM_VFD_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VFD70 |  | uCM_VFD_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VFD755 |  | uCM_VFD_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VFDCH |  | uCM_VFD_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VPR |  | uCM_VPR_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_VSL |  | uCM_V2W_V3[10] |  | (Constant := false, ExternalAccess := Read Only)
TAG |  | CM_WSGE |  | uCM_WS_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CM_WSP |  | uCM_WS_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | CurrentHour |  | REAL |  | (RADIX := Float, Constant := false, ExternalAccess := Read/Write)
TAG |  | DateTimeDOW |  | DayOfWeek_Input |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | DelayPreset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_ADDPOT |  | uEM_ADDPOT_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_ADDPOT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_ADDPOT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_AGIT |  | uEM_AGIT_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | EM_AGIT_BLANK |  |  | EM_AGIT[0] | (ExternalAccess := Read/Write)
TAG |  | EM_AGIT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_COFEED |  | uEM_CoFeed_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_COFEED_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_COFEED_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_CONT_DLY |  | uEM_CONT_DLY_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_CONT_DLY_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_CONT_DLY_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_DLY |  | uEM_DLY_V4[500] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_DLY_SCALE |  | uEM_DLY_SCALE_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_DLY_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_DLY_SCALE_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_HOLD |  | uEM_HOLD_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_HOLD_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_HOLD_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_INERT |  | uEM_INERT_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_INERT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_INERT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_PREWEIGH |  | uEM_DLY_PREWEIGH_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PREWEIGH_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PREWEIGH_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PROMPT |  | uEM_PMPT_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PROMPT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_PROMPT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
ALIAS |  | EM_PROMPT_Tank | Tank Tank Prompt Module |  | EM_PROMPT[1] | (ExternalAccess := Read/Write)
TAG |  | EM_PRS |  | uEM_PRS_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PRS_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_PRS_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_QC |  | uEM_QC_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_QC_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_QC_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_RECIRC |  | uEM_RECIRC_V3[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_RECIRC_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_RSC_MGR |  | uEM_RSC_MGR_V3[150] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_RSC_MGR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_STATUS |  | uEM_STATUS_V1[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_STATUS_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_STATUS_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG |  | EM_TEMPJK |  | uEM_TEMPJK_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_TEMPJK_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_TEMPJK_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_TEMPVC |  | uEM_TEMPVC_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_TEMPVC_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_TEMPVC_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_VENT |  | uEM_VENT_V1[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_VENT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EM_VENT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | EP_Ctrl |  | uEP_V1[200] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EP_Ctrl1 |  | uEP_V1[1] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EP_Ctrl1_InUseBitID |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl1_InUseBitID1 |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_LoopCnt1 |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_LoopEnable1 |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_Offset1 |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_CTRL_RecipeInit |  | EP_Ctrl_V2 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EP_Ctrl_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EP_Ctrl_Size1 |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG |  | EX_REQ |  | uEX_REQ_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | EX_REQ_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_BLK01_SIS01_01 |  |  | EX_REQ[6] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_BLK01_SIS01_02 |  |  | EX_REQ[7] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_LUL01_SIS01_01 |  |  | EX_REQ[5] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_MFG01_SIS01_01 |  |  | EX_REQ[1] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_MFG01_SIS01_02 |  |  | EX_REQ[2] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_MFG01_SIS01_03 |  |  | EX_REQ[3] | (ExternalAccess := Read/Write)
ALIAS |  | EX_REQ_PC_MFG01_SIS01_04 |  |  | EX_REQ[4] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_86306 |  |  | CM_AIN[22] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_87305 |  |  | CM_AIN[23] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_88305 |  |  | CM_AIN[24] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_89603 |  |  | CM_AIN[70] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_89703 |  |  | CM_AIN[71] | (ExternalAccess := Read/Write)
ALIAS |  | FIS_89803 |  |  | CM_AIN[72] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_31016 |  |  | CM_DI[135] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_31051 |  |  | CM_DI[89] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_31082 |  |  | CM_DI[126] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_32302 |  |  | CM_DI[90] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_39159 |  |  | CM_DI[127] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_39203 |  |  | CM_DI[111] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_39356 |  |  | CM_DI[136] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_40302 |  |  | CM_DI[52] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_41302 |  |  | CM_DI[53] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_42302 |  |  | CM_DI[54] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_43006 |  |  | CM_DI[55] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_44006 |  |  | CM_DI[56] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_45005 |  |  | CM_DI[57] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_80303 |  |  | CM_DI[19] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_80603 |  |  | CM_DI[20] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_81305 |  |  | CM_DI[171] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_82303 |  |  | CM_DI[30] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_83303 |  |  | CM_DI[31] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_84303 |  |  | CM_DI[32] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_85303 |  |  | CM_DI[33] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89103 |  |  | CM_DI[180] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89203 |  |  | CM_DI[181] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89252 |  |  | CM_DI[172] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89303 |  |  | CM_DI[182] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89352 |  |  | CM_DI[173] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89403 |  |  | CM_DI[183] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89503 |  |  | CM_DI[184] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_89555 |  |  | CM_DI[137] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_90003 |  |  | CM_DI[160] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_91007 |  |  | CM_DI[161] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_91355 |  |  | CM_DI[162] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_91507 |  |  | CM_DI[163] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_96302 |  |  | CM_DI[15] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_96402 |  |  | CM_DI[16] | (ExternalAccess := Read/Write)
ALIAS |  | FSL_99303 |  |  | CM_DI[91] | (ExternalAccess := Read/Write)
TAG |  | GlobalComm |  | SM_COMM |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | GlobalInit |  | uSM_Init_V3 |  | (Constant := false, ExternalAccess := None)
TAG |  | HourCounter |  | COUNTER |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | HoursInWeek | Number of Hours Of Week$N120=5days$N168=7days | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | HourTimer |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | HS_30101 |  |  | CM_DI[154] | (ExternalAccess := Read/Write)
ALIAS |  | HS_31101 |  |  | CM_DI[138] | (ExternalAccess := Read/Write)
ALIAS |  | HS_31402 |  |  | CM_DI[92] | (ExternalAccess := Read/Write)
ALIAS |  | HS_32101 |  |  | CM_DI[112] | (ExternalAccess := Read/Write)
ALIAS |  | HS_32303 |  |  | CM_DI[128] | (ExternalAccess := Read/Write)
ALIAS |  | HS_33101 |  |  | CM_DI[113] | (ExternalAccess := Read/Write)
ALIAS |  | HS_33305 |  |  | CM_DI[93] | (ExternalAccess := Read/Write)
ALIAS |  | HS_34101 |  |  | CM_DI[114] | (ExternalAccess := Read/Write)
ALIAS |  | HS_34304 |  |  | CM_DI[94] | (ExternalAccess := Read/Write)
ALIAS |  | HS_35101 |  |  | CM_DI[115] | (ExternalAccess := Read/Write)
ALIAS |  | HS_35304 |  |  | CM_DI[95] | (ExternalAccess := Read/Write)
ALIAS |  | HS_39101 |  |  | CM_DI[139] | (ExternalAccess := Read/Write)
ALIAS |  | HS_39501 |  |  | CM_DI[140] | (ExternalAccess := Read/Write)
ALIAS |  | HS_39801 |  |  | CM_DI[141] | (ExternalAccess := Read/Write)
ALIAS |  | HS_40101 |  |  | CM_DI[71] | (ExternalAccess := Read/Write)
ALIAS |  | HS_40304 |  |  | CM_DI[58] | (ExternalAccess := Read/Write)
ALIAS |  | HS_41101 |  |  | CM_DI[72] | (ExternalAccess := Read/Write)
ALIAS |  | HS_41305 |  |  | CM_DI[59] | (ExternalAccess := Read/Write)
ALIAS |  | HS_42101 |  |  | CM_DI[73] | (ExternalAccess := Read/Write)
ALIAS |  | HS_42304 |  |  | CM_DI[60] | (ExternalAccess := Read/Write)
ALIAS |  | HS_43007 |  |  | CM_DI[61] | (ExternalAccess := Read/Write)
ALIAS |  | HS_44007 |  |  | CM_DI[62] | (ExternalAccess := Read/Write)
ALIAS |  | HS_45006 |  |  | CM_DI[63] | (ExternalAccess := Read/Write)
ALIAS |  | HS_80301 |  |  | CM_DI[21] | (ExternalAccess := Read/Write)
ALIAS |  | HS_80601 |  |  | CM_DI[22] | (ExternalAccess := Read/Write)
ALIAS |  | HS_81304 |  |  | CM_DI[174] | (ExternalAccess := Read/Write)
ALIAS |  | HS_82301 |  |  | CM_DI[34] | (ExternalAccess := Read/Write)
ALIAS |  | HS_83301 |  |  | CM_DI[35] | (ExternalAccess := Read/Write)
ALIAS |  | HS_84301 |  |  | CM_DI[36] | (ExternalAccess := Read/Write)
ALIAS |  | HS_85301 |  |  | CM_DI[37] | (ExternalAccess := Read/Write)
ALIAS |  | HS_86301 |  |  | CM_DI[80] | (ExternalAccess := Read/Write)
ALIAS |  | HS_87301 |  |  | CM_DI[81] | (ExternalAccess := Read/Write)
ALIAS |  | HS_88301 |  |  | CM_DI[82] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89104 |  |  | CM_DI[185] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89204 |  |  | CM_DI[186] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89253 |  |  | CM_DI[178] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89304 |  |  | CM_DI[187] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89353 |  |  | CM_DI[179] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89404 |  |  | CM_DI[188] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89504 |  |  | CM_DI[189] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89604 |  |  | CM_DI[190] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89704 |  |  | CM_DI[191] | (ExternalAccess := Read/Write)
ALIAS |  | HS_89804 |  |  | CM_DI[192] | (ExternalAccess := Read/Write)
ALIAS |  | HS_90302 |  |  | CM_DI[164] | (ExternalAccess := Read/Write)
ALIAS |  | HS_91302 |  |  | CM_DI[165] | (ExternalAccess := Read/Write)
ALIAS |  | HS_91352 |  |  | CM_DI[166] | (ExternalAccess := Read/Write)
ALIAS |  | HS_91702 |  |  | CM_DI[167] | (ExternalAccess := Read/Write)
ALIAS |  | HS_96304 |  |  | CM_DI[17] | (ExternalAccess := Read/Write)
ALIAS |  | HS_96404 |  |  | CM_DI[18] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99305 |  |  | CM_DI[96] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99908 |  |  | CM_DI[38] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99909 |  |  | CM_DI[23] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99910 |  |  | CM_DI[68] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99911 |  |  | CM_DI[69] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99912 |  |  | CM_DI[70] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99913 |  |  | CM_DI[24] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99914 |  |  | CM_DI[87] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99915 |  |  | CM_DI[1] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99916 |  |  | CM_DI[97] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99917 |  |  | CM_DI[116] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99918 |  |  | CM_DI[129] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99919 |  |  | CM_DI[153] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99920 |  |  | CM_DI[155] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99921 |  |  | CM_DI[156] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99922 |  |  | CM_DI[193] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99923 |  |  | CM_DI[194] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99938 |  |  | CM_DI[2] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99941 |  |  | CM_DI[3] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99942 |  |  | CM_DI[4] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99943 |  |  | CM_DI[5] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99944 |  |  | CM_DI[6] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99950 |  |  | CM_DI[7] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99951 |  |  | CM_DI[8] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99952 |  |  | CM_DI[9] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99953 |  |  | CM_DI[10] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99954 |  |  | CM_DI[11] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99955 |  |  | CM_DI[12] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99956 |  |  | CM_DI[13] | (ExternalAccess := Read/Write)
ALIAS |  | HS_99957 |  |  | CM_DI[14] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_39404 |  |  | CM_AIN[54] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_39705 |  |  | CM_AIN[55] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_86004 |  |  | CM_AIN[25] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_87002 |  |  | CM_AIN[26] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_88005 |  |  | CM_AIN[27] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_96204 |  |  | CM_AIN[1] | (ExternalAccess := Read/Write)
ALIAS |  | LIS_98200 |  |  | CM_AIN[29] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_30004 |  |  | CM_DI[157] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_31003 |  |  | CM_DI[145] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_32005 |  |  | CM_DI[118] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_33016 |  |  | CM_DI[119] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_34002 |  |  | CM_DI[120] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_35015 |  |  | CM_DI[121] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_39002 |  |  | CM_DI[146] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_40017 |  |  | CM_DI[74] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_41008 |  |  | CM_DI[75] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_42013 |  |  | CM_DI[76] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_43004 |  |  | CM_DI[48] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_44004 |  |  | CM_DI[49] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_45003 |  |  | CM_DI[50] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_46002 |  |  | CM_DI[195] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_80005 |  |  | CM_DI[27] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_82005 |  |  | CM_DI[39] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_83005 |  |  | CM_DI[45] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_84004 |  |  | CM_DI[46] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_85005 |  |  | CM_DI[47] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_90002 |  |  | CM_DI[168] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_91002 |  |  | CM_DI[169] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_91502 |  |  | CM_DI[170] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99005 |  |  | CM_DI[102] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99981 |  |  | CM_DI[28] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99982 |  |  | CM_DI[40] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99983 |  |  | CM_DI[51] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99984 |  |  | CM_DI[64] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99985 |  |  | CM_DI[83] | (ExternalAccess := Read/Write)
ALIAS |  | LSHH_99986 |  |  | CM_DI[103] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_31399 |  |  | CM_DI[142] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_39199 |  |  | CM_DI[130] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_39299 |  |  | CM_DI[117] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_39399 |  |  | CM_DI[143] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_40222 |  |  | CM_DI[98] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_41208 |  |  | CM_DI[99] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_42252 |  |  | CM_DI[100] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_89599 |  |  | CM_DI[144] | (ExternalAccess := Read/Write)
ALIAS |  | LSH_99599 |  |  | CM_DI[101] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_30104 |  |  | CM_DI[158] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_31104 |  |  | CM_DI[147] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_32104 |  |  | CM_DI[131] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_33104 |  |  | CM_DI[132] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_34104 |  |  | CM_DI[133] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_35104 |  |  | CM_DI[134] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_39504 |  |  | CM_DI[148] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_39804 |  |  | CM_DI[149] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_40104 |  |  | CM_DI[77] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_41104 |  |  | CM_DI[78] | (ExternalAccess := Read/Write)
ALIAS |  | LSLL_42104 |  |  | CM_DI[79] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_31409 |  |  | CM_DI[104] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_32307 |  |  | CM_DI[105] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_33302 |  |  | CM_DI[106] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_34302 |  |  | CM_DI[107] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_35302 |  |  | CM_DI[108] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_43303 |  |  | CM_DI[65] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_44303 |  |  | CM_DI[66] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_45309 |  |  | CM_DI[67] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_80307 |  |  | CM_DI[25] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_80607 |  |  | CM_DI[26] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_81307 |  |  | CM_DI[175] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_89108 |  |  | CM_DI[196] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_89258 |  |  | CM_DI[176] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_89357 |  |  | CM_DI[177] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_98005 |  |  | CM_DI[109] | (ExternalAccess := Read/Write)
ALIAS |  | LSL_99308 |  |  | CM_DI[110] | (ExternalAccess := Read/Write)
TAG |  | MiscDINT |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | MIS_31141_ES |  |  | CM_DOUT[27] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_31401_ES |  |  | CM_DOUT[28] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_32141_ES |  |  | CM_DOUT[29] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_32304_ES |  |  | CM_DOUT[30] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_40141_ES |  |  | CM_DOUT[54] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_41141_ES |  |  | CM_DOUT[55] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_42141_ES |  |  | CM_DOUT[56] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_43008_ES |  |  | CM_DOUT[31] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_44008_ES |  |  | CM_DOUT[32] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_45007_ES |  |  | CM_DOUT[33] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_80302_ES |  |  | CM_DOUT[34] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_80602_ES |  |  | CM_DOUT[35] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_81303_ES |  |  | CM_DOUT[36] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_82302_ES |  |  | CM_DOUT[37] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_83302_ES |  |  | CM_DOUT[38] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_84302_ES |  |  | CM_DOUT[39] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_85302_ES |  |  | CM_DOUT[40] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_89205_ES |  |  | CM_DOUT[41] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_89305_ES |  |  | CM_DOUT[42] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_89354_ES |  |  | CM_DOUT[43] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_89405_ES |  |  | CM_DOUT[44] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_89505_ES |  |  | CM_DOUT[45] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_90301_ES |  |  | CM_DOUT[46] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_91301_ES |  |  | CM_DOUT[47] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_91351_ES |  |  | CM_DOUT[48] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_91701_ES |  |  | CM_DOUT[49] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_96303_ES |  |  | CM_DOUT[50] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_96403_ES |  |  | CM_DOUT[51] | (ExternalAccess := Read/Write)
ALIAS |  | MIS_99301_ES |  |  | CM_DOUT[52] | (ExternalAccess := Read/Write)
TAG |  | MM_CIR |  | uMM_CIR_V1[100] |  | (Constant := false, ExternalAccess := Read Only)
TAG |  | ModuleRef |  | uSM_GLB_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | ONS |  | DINT[10] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_BLK01_SIS01_01 |  | uPC_TOR_BLK01_SIS01_01 |  | (Producer := "TOR_BLK01", RemoteTag := "PC_BLK01_SIS01_01", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_BLK01_SIS01_02 |  | uPC_TOR_BLK01_SIS01_02 |  | (Producer := "TOR_BLK01", RemoteTag := "PC_BLK01_SIS01_02", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_BLK01_SIS01_ConnStat | Produced/Consumed Connection Status$N1 = Good$N0 = Bad | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_LUL01_SIS01_01 |  | uPC_TOR_LUL01_SIS01_01 |  | (Producer := "TOR_LUL01", RemoteTag := "PC_LUL01_SIS01_01", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_LUL01_SIS01_ConnStat | Produced/Consumed Connection Status$N1 = Good$N0 = Bad | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_MFG01_SIS01_01 |  | uPC_TOR_MFG01_SIS01_01 |  | (Producer := "TOR_MFG01", RemoteTag := "PC_MFG01_SIS01_01", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_MFG01_SIS01_02 |  | uPC_TOR_MFG01_SIS01_02 |  | (Producer := "TOR_MFG01", RemoteTag := "PC_MFG01_SIS01_02", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_MFG01_SIS01_03 |  | uPC_TOR_MFG01_SIS01_03 |  | (Producer := "TOR_MFG01", RemoteTag := "PC_MFG01_SIS01_03", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_MFG01_SIS01_04 |  | uPC_TOR_MFG01_SIS01_04 |  | (Producer := "TOR_MFG01", RemoteTag := "PC_MFG01_SIS01_04", RemoteFile := 0, RPI := 20, Unicast := true, ExternalAccess := Read/Write)
TAG |  | PC_MFG01_SIS01_ConnStat | Produced/Consumed Connection Status$N1 = Good$N0 = Bad | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_SIS01_BLK01_01 |  | uPC_TOR_BLK01_SIS01_01 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_BLK01_02 |  | uPC_TOR_BLK01_SIS01_02 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_LUL01_01 |  | uPC_TOR_LUL01_SIS01_01 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_MFG01_01 |  | uPC_TOR_MFG01_SIS01_01 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_MFG01_02 |  | uPC_TOR_MFG01_SIS01_02 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_MFG01_03 |  | uPC_TOR_MFG01_SIS01_03 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_SIS01_MFG01_04 |  | uPC_TOR_MFG01_SIS01_04 |  | (ProduceCount := 1, ProgrammaticallySendEventTrigger := false, UnicastPermitted := true, Constant := false, ExternalAccess := Read/Write, MinimumRPI := 0.200, MaximumRPI := 536870.900, DefaultRPI := 0)
TAG |  | PC_TOR_BLK01_SIS01_01_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_BLK01_SIS01_02_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_LUL01_SIS01_01_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_MFG01_SIS01_01_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_MFG01_SIS01_02_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_MFG01_SIS01_03_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | PC_TOR_MFG01_SIS01_04_ConnStat |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | pc_V2W_Array |  | uCM_V2W_V3[100] |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | PIS_30001 |  |  | CM_AIN[62] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_31002 |  |  | CM_AIN[56] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_31063 |  |  | CM_AIN[57] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_32003 |  |  | CM_AIN[46] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_33017 |  |  | CM_AIN[47] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_33306 |  |  | CM_AIN[39] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_34001 |  |  | CM_AIN[48] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_34306 |  |  | CM_AIN[40] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_35012 |  |  | CM_AIN[49] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_35305 |  |  | CM_AIN[41] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_39401 |  |  | CM_AIN[58] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_39701 |  |  | CM_AIN[60] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_40020 |  |  | CM_AIN[19] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_40305 |  |  | CM_AIN[16] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_41001 |  |  | CM_AIN[20] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_41303 |  |  | CM_AIN[17] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_42014 |  |  | CM_AIN[21] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_42305 |  |  | CM_AIN[18] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_80017 |  |  | CM_AIN[2] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_82002 |  |  | CM_AIN[12] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_83003 |  |  | CM_AIN[13] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_84003 |  |  | CM_AIN[14] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_85002 |  |  | CM_AIN[15] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_86012 |  |  | CM_AIN[30] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_86303 |  |  | CM_AIN[31] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_87001 |  |  | CM_AIN[32] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_87303 |  |  | CM_AIN[33] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_88003 |  |  | CM_AIN[34] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_88303 |  |  | CM_AIN[35] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_89112 |  |  | CM_AIN[65] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_89113 |  |  | CM_AIN[66] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_89606 |  |  | CM_AIN[67] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_89706 |  |  | CM_AIN[68] | (ExternalAccess := Read/Write)
ALIAS |  | PIS_89806 |  |  | CM_AIN[69] | (ExternalAccess := Read/Write)
ALIAS |  | PL_DevDevices |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_EnetDevices |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_MOT_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z1_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z2_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z2_002 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z2_021 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z3_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z4_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z4_021 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z5_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z6_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z6_021 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z6_031 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z6_041 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z6_061 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_Z7_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_ZA_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_JBS_ZI_001 |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_LocalRack |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_MSGDevices |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
ALIAS |  | PL_SystemFaults |  |  | PL_SystemWide | (ExternalAccess := Read/Write)
TAG |  | PL_SystemWide |  | uSM_InUseBy_V3 |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | PSE_30009 |  |  | CM_DI[159] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_31004 |  |  | CM_DI[150] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_32004 |  |  | CM_DI[122] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_33018 |  |  | CM_DI[123] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_34003 |  |  | CM_DI[124] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_35016 |  |  | CM_DI[125] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_39409 |  |  | CM_DI[151] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_39710 |  |  | CM_DI[152] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_80016 |  |  | CM_DI[29] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_82010 |  |  | CM_DI[41] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_83010 |  |  | CM_DI[42] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_84010 |  |  | CM_DI[43] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_85010 |  |  | CM_DI[44] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_86010 |  |  | CM_DI[84] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_87009 |  |  | CM_DI[85] | (ExternalAccess := Read/Write)
ALIAS |  | PSE_88009 |  |  | CM_DI[86] | (ExternalAccess := Read/Write)
TAG |  | RecipeInit_ONS |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | sBaseBarcode | Static Strings | udsBarcodeStrings |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | sContainer |  | udsContTracking[50] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | SecondsInWeek | Number Of Milli-Seconds in Week | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | SF_HMI_COMM_SIS01 |  |  | CM_SF[1] | (ExternalAccess := Read/Write)
ALIAS |  | SF_pc_BLK01_SIS01 |  |  | CM_SF[2] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_BLK01_SIS01_01 |  |  | CM_SF[3] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_BLK01_SIS01_02 |  |  | CM_SF[4] | (ExternalAccess := Read/Write)
ALIAS |  | SF_pc_LUL01_SIS01 |  |  | CM_SF[3] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_LUL01_SIS01_01 |  |  | CM_SF[5] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_MFG01_SIS01_01 |  |  | CM_SF[6] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_MFG01_SIS01_02 |  |  | CM_SF[7] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_MFG01_SIS01_03 |  |  | CM_SF[8] | (ExternalAccess := Read/Write)
ALIAS |  | SF_PC_MFG01_SIS01_04 |  |  | CM_SF[9] | (ExternalAccess := Read/Write)
ALIAS |  | SF_T981 |  |  | CM_SF[1] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_30101_ES |  |  | CM_DOUT[1] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_31101_ES |  |  | CM_DOUT[2] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_32101_ES |  |  | CM_DOUT[3] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_33101_ES |  |  | CM_DOUT[4] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_33304_ES |  |  | CM_DOUT[5] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_34101_ES |  |  | CM_DOUT[6] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_34305_ES |  |  | CM_DOUT[7] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_35101_ES |  |  | CM_DOUT[8] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_35303_ES |  |  | CM_DOUT[9] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_39101_ES |  |  | CM_DOUT[10] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_39501_ES |  |  | CM_DOUT[11] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_39801_ES |  |  | CM_DOUT[12] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_40101_ES |  |  | CM_DOUT[13] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_40303_ES |  |  | CM_DOUT[14] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_41101_ES |  |  | CM_DOUT[15] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_41304_ES |  |  | CM_DOUT[16] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_42101_ES |  |  | CM_DOUT[17] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_42303_ES |  |  | CM_DOUT[18] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_86302_ES |  |  | CM_DOUT[19] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_87302_ES |  |  | CM_DOUT[20] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_88302_ES |  |  | CM_DOUT[21] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_89105_ES |  |  | CM_DOUT[22] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_89254_ES |  |  | CM_DOUT[23] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_89605_ES |  |  | CM_DOUT[24] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_89705_ES |  |  | CM_DOUT[25] | (ExternalAccess := Read/Write)
ALIAS |  | SIC_89805_ES |  |  | CM_DOUT[26] | (ExternalAccess := Read/Write)
TAG |  | sim_timer |  | TIMER[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | SI_DLY |  | SM_SourceInfoTable_V2[70] |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | SI_DLY_BLANK |  |  | SI_DLY[0] | (ExternalAccess := Read/Write)
TAG |  | SM_CC |  | uSM_CC_V3[10] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | SM_PREACT |  | SM_Preact[1000] |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | Source | Source Properties Table | SM_SourceData_V2 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | SourceInfoTables |  | SM_SourceInfoTable_V2[50] |  | (Constant := false, ExternalAccess := None)
TAG |  | SpareDINT | Spare DINTs For Testing | DINT[100] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | SpareReal | Spare Reals for Testing | REAL[100] |  | (RADIX := Float, Constant := false, ExternalAccess := Read/Write)
TAG |  | StartWeek | Start Week Command | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | sTimeDate |  | STRING |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | sTimeDate_Convrt |  | udsDateTime_String |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | sWALL_CLOCK |  | udsDateTime |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | System_Alarm | A Device is in Alarm For HMI Display | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | SZ_EMModules |  |  | CM_SZONE[2] | (ExternalAccess := Read/Write)
ALIAS |  | SZ_SystemWide |  |  | CM_SZONE[1] | (ExternalAccess := Read/Write)
TAG |  | TankNumberIndex |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | Time_Sync | Time Synchronization Values from the SCADA | DINT[10] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
COMMENT |  | Time_Sync | Current Year (0-9999) from HMI |  | Time_Sync[0]
TAG |  | Time_Sync_Buffer | Buffer the Time Date Information from the SCADA for Writing to the PLC Clock | DINT[10] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | Time_Sync_Trigger | Time Synchronization Trigger from the SCADA | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS |  | TIS_31010 |  |  | CM_AIN[50] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_32035 |  |  | CM_AIN[42] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_33020 |  |  | CM_AIN[43] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_34006 |  |  | CM_AIN[44] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_35024 |  |  | CM_AIN[51] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_39408 |  |  | CM_AIN[52] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_39709 |  |  | CM_AIN[53] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_47507 |  |  | CM_AIN[45] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_82009 |  |  | CM_AIN[7] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_83009 |  |  | CM_AIN[8] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_83304 |  |  | CM_AIN[9] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_84009 |  |  | CM_AIN[10] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_85009 |  |  | CM_AIN[11] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_86008 |  |  | CM_AIN[36] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_87008 |  |  | CM_AIN[37] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_88008 |  |  | CM_AIN[38] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_91006 |  |  | CM_AIN[63] | (ExternalAccess := Read/Write)
ALIAS |  | TIS_91603 |  |  | CM_AIN[64] | (ExternalAccess := Read/Write)
TAG |  | tmrEOWHold |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | TSHH_31105 |  |  | CM_DI[197] | (ExternalAccess := Read/Write)
ALIAS |  | TSHH_32105 |  |  | CM_DI[198] | (ExternalAccess := Read/Write)
TAG |  | UnitComplete |  | STRING |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | WatchDog | This is used by Batch | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | WatchDogLastReset |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | WatchDogLastTimeDate |  | STRING |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | WatchDogLossAlarm |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | WD_MaxLastReset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | WD_MaxLossOfComm_Time |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG |  | WeekTimer |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
ALIAS |  | XIS_30003 |  |  | CM_V2W[86] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_30024 |  |  | CM_V2W[87] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_30027 |  |  | CM_V2W[105] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31019 |  |  | CM_V2W[88] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31024 |  |  | CM_V2W[89] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31029 |  |  | CM_V2W[75] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31041 |  |  | CM_V2W[67] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31053 |  |  | CM_V2W[90] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31073 |  |  | CM_V2W[91] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31077 |  |  | CM_V2W[68] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31078 |  |  | CM_V2W[69] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_31301 |  |  | CM_V2W[92] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_32002 |  |  | CM_V2W[76] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_32010 |  |  | CM_V2W[46] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_32012 |  |  | CM_V2W[47] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_32021 |  |  | CM_V2W[77] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_32306 |  |  | CM_V2W[48] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33010 |  |  | CM_V2W[78] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33011 |  |  | CM_V2W[79] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33014 |  |  | CM_V2W[80] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33015 |  |  | CM_V2W[70] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33034 |  |  | CM_V2W[49] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33040 |  |  | CM_V2W[50] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_33307 |  |  | CM_V2W[51] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34004 |  |  | CM_V2W[52] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34013 |  |  | CM_V2W[53] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34024 |  |  | CM_V2W[81] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34027 |  |  | CM_V2W[54] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34030 |  |  | CM_V2W[71] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_34307 |  |  | CM_V2W[55] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35001 |  |  | CM_V2W[56] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35003 |  |  | CM_V2W[82] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35004 |  |  | CM_V2W[57] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35008 |  |  | CM_V2W[83] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35035 |  |  | CM_V2W[58] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_35047 |  |  | CM_V2W[72] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39008 |  |  | CM_V2W[93] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39031 |  |  | CM_V2W[84] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39033 |  |  | CM_V2W[73] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39157 |  |  | CM_V2W[85] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39207 |  |  | CM_V2W[74] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39358 |  |  | CM_V2W[94] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39427 |  |  | CM_V2W[95] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39435 |  |  | CM_V2W[98] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39441 |  |  | CM_V2W[103] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39442 |  |  | CM_V2W[96] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39443 |  |  | CM_V2W[97] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39727 |  |  | CM_V2W[99] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39741 |  |  | CM_V2W[104] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39742 |  |  | CM_V2W[100] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_39743 |  |  | CM_V2W[101] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_40030 |  |  | CM_V2W[30] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_40201 |  |  | CM_V2W[59] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_40308 |  |  | CM_V2W[31] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_41020 |  |  | CM_V2W[32] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_41201 |  |  | CM_V2W[60] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_42027 |  |  | CM_V2W[33] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_42201 |  |  | CM_V2W[61] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_47505 |  |  | CM_V2W[62] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_80012 |  |  | CM_V2W[4] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_80018 |  |  | CM_V2W[5] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82001 |  |  | CM_V2W[22] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82013 |  |  | CM_V2W[23] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82015 |  |  | CM_V2W[6] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82041 |  |  | CM_V2W[18] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82042 |  |  | CM_V2W[7] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_82043 |  |  | CM_V2W[8] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83001 |  |  | CM_V2W[24] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83013 |  |  | CM_V2W[9] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83016 |  |  | CM_V2W[25] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83041 |  |  | CM_V2W[19] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83042 |  |  | CM_V2W[10] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_83043 |  |  | CM_V2W[11] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84002 |  |  | CM_V2W[12] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84013 |  |  | CM_V2W[26] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84016 |  |  | CM_V2W[27] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84041 |  |  | CM_V2W[20] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84042 |  |  | CM_V2W[13] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_84043 |  |  | CM_V2W[14] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85013 |  |  | CM_V2W[28] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85016 |  |  | CM_V2W[29] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85017 |  |  | CM_V2W[15] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85041 |  |  | CM_V2W[21] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85042 |  |  | CM_V2W[16] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_85043 |  |  | CM_V2W[17] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_86009 |  |  | CM_V2W[34] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_86013 |  |  | CM_V2W[35] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_86016 |  |  | CM_V2W[36] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_86201 |  |  | CM_V2W[37] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_87003 |  |  | CM_V2W[38] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_87012 |  |  | CM_V2W[39] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_87014 |  |  | CM_V2W[40] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_87201 |  |  | CM_V2W[41] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_88012 |  |  | CM_V2W[42] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_88014 |  |  | CM_V2W[43] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_88015 |  |  | CM_V2W[44] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_88201 |  |  | CM_V2W[45] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_89554 |  |  | CM_V2W[102] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_90001 |  |  | CM_V2W[106] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_91001 |  |  | CM_V2W[107] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_91201 |  |  | CM_V2W[108] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_91501 |  |  | CM_V2W[109] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_91506 |  |  | CM_V2W[110] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_91601 |  |  | CM_V2W[111] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_96201 |  |  | CM_V2W[1] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_96202 |  |  | CM_V2W[2] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_96209 |  |  | CM_V2W[3] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_99002 |  |  | CM_V2W[63] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_99004 |  |  | CM_V2W[64] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_99302 |  |  | CM_V2W[65] | (ExternalAccess := Read/Write)
ALIAS |  | XIS_99501 |  |  | CM_V2W[66] | (ExternalAccess := Read/Write)
ALIAS |  | XI_98102 |  |  | CM_DI[88] | (ExternalAccess := Read/Write)
ALIAS |  | XS_98500 |  |  | CM_DOUT[53] | (ExternalAccess := Read/Write)
ALIAS |  | ZL_EnetDevices |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_MOT_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z1_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z2_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z2_002 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z2_021 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z3_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z4_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z4_021 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z5_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z6_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z6_021 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z6_031 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z6_041 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z6_061 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_Z7_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_ZA_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_JBS_ZI_001 |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_LocalRack |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_MSGDevices |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
ALIAS |  | ZL_SystemFaults |  |  | SZ_SystemWide.LNK | (ExternalAccess := Read Only)
TAG |  | ZL_SystemWide |  | CM_ZON_LNK_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG |  | PLCDevices_MSG |  | MESSAGE |  | (ExternalAccess := Read Only, MessageType := Unconfigured, RequestedLength := 1, CommTypeCode := 0, LocalIndex := 0)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Active_Prompt_Lookup | ActivePrompt_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | ActivePrompt_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_ADDPOT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_AGIT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_CONT_DLY_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_DLY_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_DLY_SCALE_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_INERT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_PREWEIGH_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_PROMPT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_PRS_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_QC_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_STATUS_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_TEMPJK_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_TEMPVC_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | EM_VENT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | PromptClearLoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | Prompt_Count |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | Active_Prompt_Lookup | UpdateTmr |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Analog_IN | CM_FIS_86306 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_FIS_87305 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_FIS_88305 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_FIS_89603 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_FIS_89703 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_FIS_89803 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_39404 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_39705 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_86004 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_87002 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_88005 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_96204 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_LIS_98200 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_30001 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_31002 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_31063 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_32003 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_33017 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_33306 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_34001 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_34306 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_35012 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_35305 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_39401 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_39701 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_40020 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_40305 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_41001 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_41303 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_42014 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_42305 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_80017 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_82002 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_83003 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_84003 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_85002 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_86012 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_86303 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_87001 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_87303 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_88003 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_88303 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_89112 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_89113 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_89606 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_89706 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_PIS_89806 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_31010 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_32035 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_33020 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_34006 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_35024 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_39408 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_39709 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_47507 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_82009 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_83009 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_83304 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_84009 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_85009 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_86008 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_87008 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_88008 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_91006 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Analog_IN | CM_TIS_91603 |  | CM_AIN_V3 |  | (Constant := false, ExternalAccess := Read Only)
ALIAS | Analog_IN | FLT_I_FIS_86306 |  |  | JBS_Z5_001:13:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_FIS_87305 |  |  | JBS_Z5_001:13:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_FIS_88305 |  |  | JBS_Z5_001:13:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_FIS_89603 |  |  | JBS_ZI_001:5:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_FIS_89703 |  |  | JBS_ZI_001:5:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_FIS_89803 |  |  | JBS_ZI_001:5:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_39404 |  |  | JBS_Z6_041:20:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_39705 |  |  | JBS_Z6_041:20:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_86004 |  |  | JBS_Z5_001:13:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_87002 |  |  | JBS_Z5_001:14:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_88005 |  |  | JBS_Z5_001:14:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_96204 |  |  | JBS_Z1_001:6:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_LIS_98200 |  |  | JBS_Z5_001:14:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_30001 |  |  | JBS_Z6_061:5:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_31002 |  |  | JBS_Z6_041:20:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_31063 |  |  | JBS_Z6_041:20:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_32003 |  |  | JBS_Z6_021:11:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_33017 |  |  | JBS_Z6_021:11:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_33306 |  |  | JBS_Z6_001:20:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_34001 |  |  | JBS_Z6_021:11:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_34306 |  |  | JBS_Z6_001:20:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_35012 |  |  | JBS_Z6_021:11:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_35305 |  |  | JBS_Z6_001:20:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_39401 |  |  | JBS_Z6_041:21:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_39701 |  |  | JBS_Z6_041:21:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_40020 |  |  | JBS_Z4_021:7:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_40305 |  |  | JBS_Z4_001:4:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_41001 |  |  | JBS_Z4_021:7:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_41303 |  |  | JBS_Z4_001:4:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_42014 |  |  | JBS_Z4_021:7:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_42305 |  |  | JBS_Z4_001:4:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_80017 |  |  | JBS_Z2_001:6:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_82002 |  |  | JBS_Z2_021:10:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_83003 |  |  | JBS_Z2_021:10:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_84003 |  |  | JBS_Z2_021:10:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_85002 |  |  | JBS_Z2_021:10:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_86012 |  |  | JBS_Z5_001:15:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_86303 |  |  | JBS_Z5_001:15:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_87001 |  |  | JBS_Z5_001:15:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_87303 |  |  | JBS_Z5_001:15:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_88003 |  |  | JBS_Z5_001:16:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_88303 |  |  | JBS_Z5_001:16:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_89112 |  |  | JBS_ZI_001:4:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_89113 |  |  | JBS_ZI_001:4:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_89606 |  |  | JBS_ZI_001:4:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_89706 |  |  | JBS_ZI_001:4:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_PIS_89806 |  |  | JBS_ZI_001:5:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_31010 |  |  | JBS_Z6_031:13:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_32035 |  |  | JBS_Z6_001:20:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_33020 |  |  | JBS_Z6_001:21:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_34006 |  |  | JBS_Z6_001:21:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_35024 |  |  | JBS_Z6_031:13:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_39408 |  |  | JBS_Z6_031:13:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_39709 |  |  | JBS_Z6_031:13:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_47507 |  |  | JBS_Z6_001:21:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_82009 |  |  | JBS_Z2_002:19:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_83009 |  |  | JBS_Z2_002:19:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_83304 |  |  | JBS_Z2_002:19:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_84009 |  |  | JBS_Z2_002:19:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_85009 |  |  | JBS_Z2_002:20:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_86008 |  |  | JBS_Z5_001:16:I.Ch03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_87008 |  |  | JBS_Z5_001:16:I.Ch04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_88008 |  |  | JBS_Z5_001:17:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_91006 |  |  | JBS_Z7_001:9:I.Ch01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | FLT_I_TIS_91603 |  |  | JBS_Z7_001:9:I.Ch02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_86306 |  |  | JBS_Z5_001:13:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_87305 |  |  | JBS_Z5_001:13:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_88305 |  |  | JBS_Z5_001:13:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_89603 |  |  | JBS_ZI_001:5:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_89703 |  |  | JBS_ZI_001:5:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_FIS_89803 |  |  | JBS_ZI_001:5:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_39404 |  |  | JBS_Z6_041:20:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_39705 |  |  | JBS_Z6_041:20:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_86004 |  |  | JBS_Z5_001:13:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_87002 |  |  | JBS_Z5_001:14:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_88005 |  |  | JBS_Z5_001:14:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_96204 |  |  | JBS_Z1_001:6:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_LIS_98200 |  |  | JBS_Z5_001:14:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_30001 |  |  | JBS_Z6_061:5:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_31002 |  |  | JBS_Z6_041:20:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_31063 |  |  | JBS_Z6_041:20:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_32003 |  |  | JBS_Z6_021:11:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_33017 |  |  | JBS_Z6_021:11:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_33306 |  |  | JBS_Z6_001:20:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_34001 |  |  | JBS_Z6_021:11:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_34306 |  |  | JBS_Z6_001:20:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_35012 |  |  | JBS_Z6_021:11:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_35305 |  |  | JBS_Z6_001:20:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_39401 |  |  | JBS_Z6_041:21:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_39701 |  |  | JBS_Z6_041:21:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_40020 |  |  | JBS_Z4_021:7:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_40305 |  |  | JBS_Z4_001:4:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_41001 |  |  | JBS_Z4_021:7:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_41303 |  |  | JBS_Z4_001:4:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_42014 |  |  | JBS_Z4_021:7:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_42305 |  |  | JBS_Z4_001:4:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_80017 |  |  | JBS_Z2_001:6:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_82002 |  |  | JBS_Z2_021:10:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_83003 |  |  | JBS_Z2_021:10:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_84003 |  |  | JBS_Z2_021:10:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_85002 |  |  | JBS_Z2_021:10:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_86012 |  |  | JBS_Z5_001:15:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_86303 |  |  | JBS_Z5_001:15:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_87001 |  |  | JBS_Z5_001:15:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_87303 |  |  | JBS_Z5_001:15:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_88003 |  |  | JBS_Z5_001:16:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_88303 |  |  | JBS_Z5_001:16:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_89112 |  |  | JBS_ZI_001:4:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_89113 |  |  | JBS_ZI_001:4:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_89606 |  |  | JBS_ZI_001:4:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_89706 |  |  | JBS_ZI_001:4:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_PIS_89806 |  |  | JBS_ZI_001:5:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_31010 |  |  | JBS_Z6_031:13:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_32035 |  |  | JBS_Z6_001:20:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_33020 |  |  | JBS_Z6_001:21:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_34006 |  |  | JBS_Z6_001:21:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_35024 |  |  | JBS_Z6_031:13:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_39408 |  |  | JBS_Z6_031:13:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_39709 |  |  | JBS_Z6_031:13:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_47507 |  |  | JBS_Z6_001:21:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_82009 |  |  | JBS_Z2_002:19:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_83009 |  |  | JBS_Z2_002:19:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_83304 |  |  | JBS_Z2_002:19:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_84009 |  |  | JBS_Z2_002:19:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_85009 |  |  | JBS_Z2_002:20:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_86008 |  |  | JBS_Z5_001:16:I.Ch03.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_87008 |  |  | JBS_Z5_001:16:I.Ch04.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_88008 |  |  | JBS_Z5_001:17:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_91006 |  |  | JBS_Z7_001:9:I.Ch01.Data | (RADIX := Float, ExternalAccess := Read/Write)
ALIAS | Analog_IN | I_TIS_91603 |  |  | JBS_Z7_001:9:I.Ch02.Data | (RADIX := Float, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Digital_IN | CM_FSL_31016 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_31051 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_31082 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_32302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_39159 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_39203 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_39356 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_40302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_41302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_42302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_43006 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_44006 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_45005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_80303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_80603 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_81305 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_82303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_83303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_84303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_85303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89103 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89203 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89252 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89352 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89403 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89503 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_89555 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_90003 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_91007 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_91355 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_91507 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_96302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_96402 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_FSL_99303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_30101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_31101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_31402 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_32101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_32303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_33101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_33305 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_34101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_34304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_35101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_35304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_39101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_39501 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_39801 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_40101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_40304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_41101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_41305 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_42101 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_42304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_43007 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_44007 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_45006 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_80301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_80601 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_81304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_82301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_83301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_84301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_85301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_86301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_87301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_88301 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89204 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89253 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89353 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89404 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89504 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89604 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89704 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_89804 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_90302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_91302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_91352 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_91702 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_96304 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_96404 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99305 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99908 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99909 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99910 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99911 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99912 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99913 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99914 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99915 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99916 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99917 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99918 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99919 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99920 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99921 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99922 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99923 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99938 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99941 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99942 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99943 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99944 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99950 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99951 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99952 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99953 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99954 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99955 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99956 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_HS_99957 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_30004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_31003 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_32005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_33016 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_34002 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_35015 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_39002 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_40017 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_41008 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_42013 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_43004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_44004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_45003 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_46002 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_80005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_82005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_83005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_84004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_85005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_90002 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_91002 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_91502 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99981 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99982 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99983 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99984 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99985 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSHH_99986 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_31399 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_39199 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_39299 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_39399 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_40222 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_41208 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_42252 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_89599 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSH_99599 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_30104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_31104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_32104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_33104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_34104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_35104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_39504 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_39804 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_40104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_41104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSLL_42104 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_31409 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_32307 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_33302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_34302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_35302 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_43303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_44303 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_45309 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_80307 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_80607 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_81307 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_89108 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_89258 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_89357 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_98005 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_LSL_99308 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_30009 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_31004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_32004 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_33018 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_34003 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_35016 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_39409 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_39710 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_80016 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_82010 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_83010 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_84010 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_85010 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_86010 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_87009 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_PSE_88009 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_IN | CM_TSHH_31105 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Digital_IN | CM_TSHH_32105 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Digital_IN | CM_XI_98102 |  | CM_DI_V5 |  | (Constant := false, ExternalAccess := Read Only)
ALIAS | Digital_IN | FLT_I_FSL_31016 |  |  | JBS_Z6_041:17:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_31051 |  |  | JBS_Z6_001:17:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_31082 |  |  | JBS_Z6_031:11:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_32302 |  |  | JBS_Z6_001:17:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_39159 |  |  | JBS_Z6_031:11:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_39203 |  |  | JBS_Z6_021:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_39356 |  |  | JBS_Z6_041:17:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_40302 |  |  | JBS_Z4_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_41302 |  |  | JBS_Z4_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_42302 |  |  | JBS_Z4_001:1:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_43006 |  |  | JBS_Z4_001:1:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_44006 |  |  | JBS_Z4_001:1:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_45005 |  |  | JBS_Z4_001:1:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_80303 |  |  | JBS_Z2_001:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_80603 |  |  | JBS_Z2_001:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_81305 |  |  | JBS_ZA_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_82303 |  |  | JBS_Z2_002:16:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_83303 |  |  | JBS_Z2_002:16:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_84303 |  |  | JBS_Z2_002:16:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_85303 |  |  | JBS_Z2_002:16:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89103 |  |  | JBS_ZI_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89203 |  |  | JBS_ZI_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89252 |  |  | JBS_ZA_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89303 |  |  | JBS_ZI_001:1:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89352 |  |  | JBS_ZA_001:1:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89403 |  |  | JBS_ZI_001:1:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89503 |  |  | JBS_ZI_001:1:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_89555 |  |  | JBS_Z6_041:17:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_90003 |  |  | JBS_Z7_001:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_91007 |  |  | JBS_Z7_001:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_91355 |  |  | JBS_Z7_001:7:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_91507 |  |  | JBS_Z7_001:7:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_96302 |  |  | JBS_Z1_001:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_96402 |  |  | JBS_Z1_001:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_FSL_99303 |  |  | JBS_Z6_001:17:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_30101 |  |  | JBS_Z6_061:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_31101 |  |  | JBS_Z6_041:17:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_31402 |  |  | JBS_Z6_001:17:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_32101 |  |  | JBS_Z6_021:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_32303 |  |  | JBS_Z6_031:11:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_33101 |  |  | JBS_Z6_021:8:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_33305 |  |  | JBS_Z6_001:17:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_34101 |  |  | JBS_Z6_021:8:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_34304 |  |  | JBS_Z6_001:17:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_35101 |  |  | JBS_Z6_021:8:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_35304 |  |  | JBS_Z6_001:18:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_39101 |  |  | JBS_Z6_041:17:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_39501 |  |  | JBS_Z6_041:17:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_39801 |  |  | JBS_Z6_041:17:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_40101 |  |  | JBS_Z4_021:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_40304 |  |  | JBS_Z4_001:1:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_41101 |  |  | JBS_Z4_021:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_41305 |  |  | JBS_Z4_001:1:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_42101 |  |  | JBS_Z4_021:5:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_42304 |  |  | JBS_Z4_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_43007 |  |  | JBS_Z4_001:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_44007 |  |  | JBS_Z4_001:2:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_45006 |  |  | JBS_Z4_001:2:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_80301 |  |  | JBS_Z2_001:4:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_80601 |  |  | JBS_Z2_001:4:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_81304 |  |  | JBS_ZA_001:1:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_82301 |  |  | JBS_Z2_002:16:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_83301 |  |  | JBS_Z2_002:16:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_84301 |  |  | JBS_Z2_002:16:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_85301 |  |  | JBS_Z2_002:16:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_86301 |  |  | JBS_Z5_001:11:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_87301 |  |  | JBS_Z5_001:11:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_88301 |  |  | JBS_Z5_001:11:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89104 |  |  | JBS_ZI_001:1:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89204 |  |  | JBS_ZI_001:1:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89253 |  |  | JBS_ZA_001:1:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89304 |  |  | JBS_ZI_001:1:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89353 |  |  | JBS_ZA_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89404 |  |  | JBS_ZI_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89504 |  |  | JBS_ZI_001:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89604 |  |  | JBS_ZI_001:2:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89704 |  |  | JBS_ZI_001:2:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_89804 |  |  | JBS_ZI_001:2:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_90302 |  |  | JBS_Z7_001:7:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_91302 |  |  | JBS_Z7_001:7:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_91352 |  |  | JBS_Z7_001:7:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_91702 |  |  | JBS_Z7_001:7:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_96304 |  |  | JBS_Z1_001:5:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_96404 |  |  | JBS_Z1_001:5:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99305 |  |  | JBS_Z6_001:18:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99908 |  |  | JBS_Z2_002:17:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99909 |  |  | JBS_Z2_001:4:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99910 |  |  | JBS_Z4_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99911 |  |  | JBS_Z4_001:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99912 |  |  | JBS_Z4_001:3:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99913 |  |  | JBS_Z2_001:4:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99914 |  |  | JBS_Z5_001:11:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99915 |  |  | JBS_MOT_001:3:I.Fault.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99916 |  |  | JBS_Z6_001:18:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99917 |  |  | JBS_Z6_021:8:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99918 |  |  | JBS_Z6_031:11:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99919 |  |  | JBS_Z6_041:19:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99920 |  |  | JBS_Z6_061:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99921 |  |  | JBS_Z6_061:4:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99922 |  |  | JBS_ZI_001:2:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99923 |  |  | JBS_ZI_001:2:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99938 |  |  | JBS_MOT_001:3:I.Fault.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99941 |  |  | JBS_MOT_001:3:I.Fault.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99942 |  |  | JBS_MOT_001:3:I.Fault.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99943 |  |  | JBS_MOT_001:3:I.Fault.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99944 |  |  | JBS_MOT_001:3:I.Fault.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99950 |  |  | JBS_MOT_001:3:I.Fault.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99951 |  |  | JBS_MOT_001:3:I.Fault.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99952 |  |  | JBS_MOT_001:3:I.Fault.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99953 |  |  | JBS_MOT_001:3:I.Fault.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99954 |  |  | JBS_MOT_001:3:I.Fault.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99955 |  |  | JBS_MOT_001:3:I.Fault.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99956 |  |  | JBS_MOT_001:3:I.Fault.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_HS_99957 |  |  | JBS_MOT_001:3:I.Fault.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_30004 |  |  | JBS_Z6_061:4:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_31003 |  |  | JBS_Z6_041:18:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_32005 |  |  | JBS_Z6_021:8:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_33016 |  |  | JBS_Z6_021:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_34002 |  |  | JBS_Z6_021:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_35015 |  |  | JBS_Z6_021:9:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_39002 |  |  | JBS_Z6_041:18:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_40017 |  |  | JBS_Z4_021:5:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_41008 |  |  | JBS_Z4_021:5:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_42013 |  |  | JBS_Z4_021:5:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_43004 |  |  | JBS_Z3_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_44004 |  |  | JBS_Z3_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_45003 |  |  | JBS_Z3_001:1:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_46002 |  |  | JBS_ZI_001:2:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_80005 |  |  | JBS_Z2_001:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_82005 |  |  | JBS_Z2_002:17:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_83005 |  |  | JBS_Z2_021:8:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_84004 |  |  | JBS_Z2_021:8:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_85005 |  |  | JBS_Z2_021:8:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_90002 |  |  | JBS_Z7_001:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_91002 |  |  | JBS_Z7_001:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_91502 |  |  | JBS_Z7_001:8:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99005 |  |  | JBS_Z6_001:18:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99981 |  |  | JBS_Z2_001:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99982 |  |  | JBS_Z2_002:17:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99983 |  |  | JBS_Z3_001:1:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99984 |  |  | JBS_Z4_001:2:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99985 |  |  | JBS_Z5_001:11:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSHH_99986 |  |  | JBS_Z6_001:19:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_31399 |  |  | JBS_Z6_041:17:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_39199 |  |  | JBS_Z6_031:11:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_39299 |  |  | JBS_Z6_021:8:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_39399 |  |  | JBS_Z6_041:18:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_40222 |  |  | JBS_Z6_001:18:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_41208 |  |  | JBS_Z6_001:18:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_42252 |  |  | JBS_Z6_001:18:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_89599 |  |  | JBS_Z6_041:18:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSH_99599 |  |  | JBS_Z6_001:18:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_30104 |  |  | JBS_Z6_061:4:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_31104 |  |  | JBS_Z6_041:18:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_32104 |  |  | JBS_Z6_031:11:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_33104 |  |  | JBS_Z6_031:11:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_34104 |  |  | JBS_Z6_031:11:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_35104 |  |  | JBS_Z6_031:12:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_39504 |  |  | JBS_Z6_041:18:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_39804 |  |  | JBS_Z6_041:18:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_40104 |  |  | JBS_Z4_021:5:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_41104 |  |  | JBS_Z4_021:5:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSLL_42104 |  |  | JBS_Z4_021:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_31409 |  |  | JBS_Z6_001:19:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_32307 |  |  | JBS_Z6_001:19:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_33302 |  |  | JBS_Z6_001:19:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_34302 |  |  | JBS_Z6_001:19:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_35302 |  |  | JBS_Z6_001:19:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_43303 |  |  | JBS_Z4_001:2:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_44303 |  |  | JBS_Z4_001:2:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_45309 |  |  | JBS_Z4_001:2:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_80307 |  |  | JBS_Z2_001:4:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_80607 |  |  | JBS_Z2_001:4:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_81307 |  |  | JBS_ZA_001:1:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_89108 |  |  | JBS_ZI_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_89258 |  |  | JBS_ZA_001:1:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_89357 |  |  | JBS_ZA_001:1:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_98005 |  |  | JBS_Z6_001:19:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_LSL_99308 |  |  | JBS_Z6_001:19:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_30009 |  |  | JBS_Z6_061:4:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_31004 |  |  | JBS_Z6_041:18:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_32004 |  |  | JBS_Z6_021:9:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_33018 |  |  | JBS_Z6_021:9:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_34003 |  |  | JBS_Z6_021:9:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_35016 |  |  | JBS_Z6_021:9:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_39409 |  |  | JBS_Z6_041:19:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_39710 |  |  | JBS_Z6_041:19:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_80016 |  |  | JBS_Z2_001:5:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_82010 |  |  | JBS_Z2_021:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_83010 |  |  | JBS_Z2_021:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_84010 |  |  | JBS_Z2_021:8:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_85010 |  |  | JBS_Z2_021:8:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_86010 |  |  | JBS_Z5_001:11:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_87009 |  |  | JBS_Z5_001:11:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_PSE_88009 |  |  | JBS_Z5_001:11:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | FLT_I_XI_98102 |  |  | JBS_Z5_001:12:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_31016 |  |  | JBS_Z6_041:17:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_31051 |  |  | JBS_Z6_001:17:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_31082 |  |  | JBS_Z6_031:11:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_32302 |  |  | JBS_Z6_001:17:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_39159 |  |  | JBS_Z6_031:11:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_39203 |  |  | JBS_Z6_021:8:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_39356 |  |  | JBS_Z6_041:17:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_40302 |  |  | JBS_Z4_001:1:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_41302 |  |  | JBS_Z4_001:1:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_42302 |  |  | JBS_Z4_001:1:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_43006 |  |  | JBS_Z4_001:1:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_44006 |  |  | JBS_Z4_001:1:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_45005 |  |  | JBS_Z4_001:1:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_80303 |  |  | JBS_Z2_001:4:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_80603 |  |  | JBS_Z2_001:4:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_81305 |  |  | JBS_ZA_001:1:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_82303 |  |  | JBS_Z2_002:16:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_83303 |  |  | JBS_Z2_002:16:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_84303 |  |  | JBS_Z2_002:16:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_85303 |  |  | JBS_Z2_002:16:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89103 |  |  | JBS_ZI_001:1:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89203 |  |  | JBS_ZI_001:1:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89252 |  |  | JBS_ZA_001:1:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89303 |  |  | JBS_ZI_001:1:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89352 |  |  | JBS_ZA_001:1:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89403 |  |  | JBS_ZI_001:1:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89503 |  |  | JBS_ZI_001:1:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_89555 |  |  | JBS_Z6_041:17:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_90003 |  |  | JBS_Z7_001:7:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_91007 |  |  | JBS_Z7_001:7:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_91355 |  |  | JBS_Z7_001:7:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_91507 |  |  | JBS_Z7_001:7:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_96302 |  |  | JBS_Z1_001:5:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_96402 |  |  | JBS_Z1_001:5:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_FSL_99303 |  |  | JBS_Z6_001:17:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_30101 |  |  | JBS_Z6_061:4:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_31101 |  |  | JBS_Z6_041:17:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_31402 |  |  | JBS_Z6_001:17:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_32101 |  |  | JBS_Z6_021:8:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_32303 |  |  | JBS_Z6_031:11:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_33101 |  |  | JBS_Z6_021:8:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_33305 |  |  | JBS_Z6_001:17:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_34101 |  |  | JBS_Z6_021:8:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_34304 |  |  | JBS_Z6_001:17:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_35101 |  |  | JBS_Z6_021:8:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_35304 |  |  | JBS_Z6_001:18:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_39101 |  |  | JBS_Z6_041:17:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_39501 |  |  | JBS_Z6_041:17:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_39801 |  |  | JBS_Z6_041:17:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_40101 |  |  | JBS_Z4_021:5:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_40304 |  |  | JBS_Z4_001:1:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_41101 |  |  | JBS_Z4_021:5:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_41305 |  |  | JBS_Z4_001:1:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_42101 |  |  | JBS_Z4_021:5:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_42304 |  |  | JBS_Z4_001:2:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_43007 |  |  | JBS_Z4_001:2:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_44007 |  |  | JBS_Z4_001:2:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_45006 |  |  | JBS_Z4_001:2:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_80301 |  |  | JBS_Z2_001:4:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_80601 |  |  | JBS_Z2_001:4:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_81304 |  |  | JBS_ZA_001:1:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_82301 |  |  | JBS_Z2_002:16:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_83301 |  |  | JBS_Z2_002:16:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_84301 |  |  | JBS_Z2_002:16:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_85301 |  |  | JBS_Z2_002:16:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_86301 |  |  | JBS_Z5_001:11:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_87301 |  |  | JBS_Z5_001:11:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_88301 |  |  | JBS_Z5_001:11:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89104 |  |  | JBS_ZI_001:1:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89204 |  |  | JBS_ZI_001:1:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89253 |  |  | JBS_ZA_001:1:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89304 |  |  | JBS_ZI_001:1:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89353 |  |  | JBS_ZA_001:2:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89404 |  |  | JBS_ZI_001:2:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89504 |  |  | JBS_ZI_001:2:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89604 |  |  | JBS_ZI_001:2:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89704 |  |  | JBS_ZI_001:2:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_89804 |  |  | JBS_ZI_001:2:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_90302 |  |  | JBS_Z7_001:7:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_91302 |  |  | JBS_Z7_001:7:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_91352 |  |  | JBS_Z7_001:7:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_91702 |  |  | JBS_Z7_001:7:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_96304 |  |  | JBS_Z1_001:5:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_96404 |  |  | JBS_Z1_001:5:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99305 |  |  | JBS_Z6_001:18:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99908 |  |  | JBS_Z2_002:17:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99909 |  |  | JBS_Z2_001:4:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99910 |  |  | JBS_Z4_001:3:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99911 |  |  | JBS_Z4_001:3:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99912 |  |  | JBS_Z4_001:3:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99913 |  |  | JBS_Z2_001:4:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99914 |  |  | JBS_Z5_001:11:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99915 |  |  | JBS_MOT_001:3:I.Data.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99916 |  |  | JBS_Z6_001:18:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99917 |  |  | JBS_Z6_021:8:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99918 |  |  | JBS_Z6_031:11:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99919 |  |  | JBS_Z6_041:19:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99920 |  |  | JBS_Z6_061:4:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99921 |  |  | JBS_Z6_061:4:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99922 |  |  | JBS_ZI_001:2:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99923 |  |  | JBS_ZI_001:2:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99938 |  |  | JBS_MOT_001:3:I.Data.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99941 |  |  | JBS_MOT_001:3:I.Data.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99942 |  |  | JBS_MOT_001:3:I.Data.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99943 |  |  | JBS_MOT_001:3:I.Data.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99944 |  |  | JBS_MOT_001:3:I.Data.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99950 |  |  | JBS_MOT_001:3:I.Data.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99951 |  |  | JBS_MOT_001:3:I.Data.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99952 |  |  | JBS_MOT_001:3:I.Data.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99953 |  |  | JBS_MOT_001:3:I.Data.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99954 |  |  | JBS_MOT_001:3:I.Data.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99955 |  |  | JBS_MOT_001:3:I.Data.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99956 |  |  | JBS_MOT_001:3:I.Data.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_HS_99957 |  |  | JBS_MOT_001:3:I.Data.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_30004 |  |  | JBS_Z6_061:4:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_31003 |  |  | JBS_Z6_041:18:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_32005 |  |  | JBS_Z6_021:8:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_33016 |  |  | JBS_Z6_021:9:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_34002 |  |  | JBS_Z6_021:9:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_35015 |  |  | JBS_Z6_021:9:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_39002 |  |  | JBS_Z6_041:18:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_40017 |  |  | JBS_Z4_021:5:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_41008 |  |  | JBS_Z4_021:5:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_42013 |  |  | JBS_Z4_021:5:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_43004 |  |  | JBS_Z3_001:1:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_44004 |  |  | JBS_Z3_001:1:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_45003 |  |  | JBS_Z3_001:1:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_46002 |  |  | JBS_ZI_001:2:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_80005 |  |  | JBS_Z2_001:5:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_82005 |  |  | JBS_Z2_002:17:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_83005 |  |  | JBS_Z2_021:8:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_84004 |  |  | JBS_Z2_021:8:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_85005 |  |  | JBS_Z2_021:8:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_90002 |  |  | JBS_Z7_001:8:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_91002 |  |  | JBS_Z7_001:8:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_91502 |  |  | JBS_Z7_001:8:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99005 |  |  | JBS_Z6_001:18:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99981 |  |  | JBS_Z2_001:5:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99982 |  |  | JBS_Z2_002:17:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99983 |  |  | JBS_Z3_001:1:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99984 |  |  | JBS_Z4_001:2:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99985 |  |  | JBS_Z5_001:11:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSHH_99986 |  |  | JBS_Z6_001:19:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_31399 |  |  | JBS_Z6_041:17:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_39199 |  |  | JBS_Z6_031:11:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_39299 |  |  | JBS_Z6_021:8:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_39399 |  |  | JBS_Z6_041:18:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_40222 |  |  | JBS_Z6_001:18:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_41208 |  |  | JBS_Z6_001:18:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_42252 |  |  | JBS_Z6_001:18:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_89599 |  |  | JBS_Z6_041:18:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSH_99599 |  |  | JBS_Z6_001:18:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_30104 |  |  | JBS_Z6_061:4:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_31104 |  |  | JBS_Z6_041:18:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_32104 |  |  | JBS_Z6_031:11:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_33104 |  |  | JBS_Z6_031:11:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_34104 |  |  | JBS_Z6_031:11:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_35104 |  |  | JBS_Z6_031:12:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_39504 |  |  | JBS_Z6_041:18:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_39804 |  |  | JBS_Z6_041:18:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_40104 |  |  | JBS_Z4_021:5:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_41104 |  |  | JBS_Z4_021:5:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSLL_42104 |  |  | JBS_Z4_021:6:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_31409 |  |  | JBS_Z6_001:19:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_32307 |  |  | JBS_Z6_001:19:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_33302 |  |  | JBS_Z6_001:19:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_34302 |  |  | JBS_Z6_001:19:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_35302 |  |  | JBS_Z6_001:19:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_43303 |  |  | JBS_Z4_001:2:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_44303 |  |  | JBS_Z4_001:2:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_45309 |  |  | JBS_Z4_001:2:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_80307 |  |  | JBS_Z2_001:4:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_80607 |  |  | JBS_Z2_001:4:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_81307 |  |  | JBS_ZA_001:1:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_89108 |  |  | JBS_ZI_001:3:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_89258 |  |  | JBS_ZA_001:1:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_89357 |  |  | JBS_ZA_001:1:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_98005 |  |  | JBS_Z6_001:19:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_LSL_99308 |  |  | JBS_Z6_001:19:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_30009 |  |  | JBS_Z6_061:4:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_31004 |  |  | JBS_Z6_041:18:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_32004 |  |  | JBS_Z6_021:9:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_33018 |  |  | JBS_Z6_021:9:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_34003 |  |  | JBS_Z6_021:9:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_35016 |  |  | JBS_Z6_021:9:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_39409 |  |  | JBS_Z6_041:19:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_39710 |  |  | JBS_Z6_041:19:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_80016 |  |  | JBS_Z2_001:5:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_82010 |  |  | JBS_Z2_021:8:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_83010 |  |  | JBS_Z2_021:8:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_84010 |  |  | JBS_Z2_021:8:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_85010 |  |  | JBS_Z2_021:8:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_86010 |  |  | JBS_Z5_001:11:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_87009 |  |  | JBS_Z5_001:11:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_PSE_88009 |  |  | JBS_Z5_001:11:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_IN | I_XI_98102 |  |  | JBS_Z5_001:12:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Digital_OUT | CM_MIS_31141_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_31401_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_32141_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_32304_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_40141_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Digital_OUT | CM_MIS_41141_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Digital_OUT | CM_MIS_42141_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Digital_OUT | CM_MIS_43008_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_44008_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_45007_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_80302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_80602_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_81303_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_82302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_83302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_84302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_85302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_89205_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_89305_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_89354_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_89405_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_89505_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_90301_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_91301_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_91351_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_91701_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_96303_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_96403_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_MIS_99301_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_30101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_31101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_32101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_33101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_33304_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_34101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_34305_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_35101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_35303_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_39101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_39501_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_39801_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_40101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_40303_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_41101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_41304_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_42101_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_42303_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_86302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_87302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_88302_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_89105_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_89254_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_89605_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_89705_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Digital_OUT | CM_SIC_89805_ES |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
ALIAS | Digital_OUT | FLT_O_MIS_31141_ES |  |  | JBS_MOT_001:2:I.Fault.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_31401_ES |  |  | JBS_MOT_001:2:I.Fault.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_32141_ES |  |  | JBS_MOT_001:2:I.Fault.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_32304_ES |  |  | JBS_MOT_001:2:I.Fault.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_43008_ES |  |  | JBS_MOT_001:2:I.Fault.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_44008_ES |  |  | JBS_MOT_001:2:I.Fault.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_45007_ES |  |  | JBS_MOT_001:2:I.Fault.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_80302_ES |  |  | JBS_MOT_001:2:I.Fault.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_80602_ES |  |  | JBS_MOT_001:2:I.Fault.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_81303_ES |  |  | JBS_MOT_001:2:I.Fault.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_82302_ES |  |  | JBS_MOT_001:2:I.Fault.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_83302_ES |  |  | JBS_MOT_001:2:I.Fault.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_84302_ES |  |  | JBS_MOT_001:2:I.Fault.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_85302_ES |  |  | JBS_MOT_001:2:I.Fault.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_89205_ES |  |  | JBS_MOT_001:2:I.Fault.14 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_89305_ES |  |  | JBS_MOT_001:2:I.Fault.15 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_89354_ES |  |  | JBS_MOT_001:2:I.Fault.16 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_89405_ES |  |  | JBS_MOT_001:2:I.Fault.17 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_89505_ES |  |  | JBS_MOT_001:2:I.Fault.18 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_90301_ES |  |  | JBS_MOT_001:2:I.Fault.19 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_91301_ES |  |  | JBS_MOT_001:2:I.Fault.20 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_91351_ES |  |  | JBS_MOT_001:2:I.Fault.21 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_91701_ES |  |  | JBS_MOT_001:2:I.Fault.22 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_96303_ES |  |  | JBS_MOT_001:2:I.Fault.23 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_96403_ES |  |  | JBS_MOT_001:2:I.Fault.24 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_MIS_99301_ES |  |  | JBS_MOT_001:2:I.Fault.25 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_30101_ES |  |  | JBS_MOT_001:1:I.Fault.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_31101_ES |  |  | JBS_MOT_001:1:I.Fault.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_32101_ES |  |  | JBS_MOT_001:1:I.Fault.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_33101_ES |  |  | JBS_MOT_001:1:I.Fault.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_33304_ES |  |  | JBS_MOT_001:1:I.Fault.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_34101_ES |  |  | JBS_MOT_001:1:I.Fault.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_34305_ES |  |  | JBS_MOT_001:1:I.Fault.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_35101_ES |  |  | JBS_MOT_001:1:I.Fault.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_35303_ES |  |  | JBS_MOT_001:1:I.Fault.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_39101_ES |  |  | JBS_MOT_001:1:I.Fault.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_39501_ES |  |  | JBS_MOT_001:1:I.Fault.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_39801_ES |  |  | JBS_MOT_001:1:I.Fault.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_40101_ES |  |  | JBS_MOT_001:1:I.Fault.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_40303_ES |  |  | JBS_MOT_001:1:I.Fault.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_41101_ES |  |  | JBS_MOT_001:1:I.Fault.14 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_41304_ES |  |  | JBS_MOT_001:1:I.Fault.15 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_42101_ES |  |  | JBS_MOT_001:1:I.Fault.16 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_42303_ES |  |  | JBS_MOT_001:1:I.Fault.17 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_86302_ES |  |  | JBS_MOT_001:1:I.Fault.18 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_87302_ES |  |  | JBS_MOT_001:1:I.Fault.19 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_88302_ES |  |  | JBS_MOT_001:1:I.Fault.20 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_89105_ES |  |  | JBS_MOT_001:1:I.Fault.21 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_89254_ES |  |  | JBS_MOT_001:1:I.Fault.22 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_89605_ES |  |  | JBS_MOT_001:1:I.Fault.23 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_89705_ES |  |  | JBS_MOT_001:1:I.Fault.24 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | FLT_O_SIC_89805_ES |  |  | JBS_MOT_001:1:I.Fault.25 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_31141_ES |  |  | JBS_MOT_001:2:O.Data.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_31401_ES |  |  | JBS_MOT_001:2:O.Data.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_32141_ES |  |  | JBS_MOT_001:2:O.Data.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_32304_ES |  |  | JBS_MOT_001:2:O.Data.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_43008_ES |  |  | JBS_MOT_001:2:O.Data.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_44008_ES |  |  | JBS_MOT_001:2:O.Data.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_45007_ES |  |  | JBS_MOT_001:2:O.Data.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_80302_ES |  |  | JBS_MOT_001:2:O.Data.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_80602_ES |  |  | JBS_MOT_001:2:O.Data.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_81303_ES |  |  | JBS_MOT_001:2:O.Data.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_82302_ES |  |  | JBS_MOT_001:2:O.Data.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_83302_ES |  |  | JBS_MOT_001:2:O.Data.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_84302_ES |  |  | JBS_MOT_001:2:O.Data.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_85302_ES |  |  | JBS_MOT_001:2:O.Data.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_89205_ES |  |  | JBS_MOT_001:2:O.Data.14 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_89305_ES |  |  | JBS_MOT_001:2:O.Data.15 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_89354_ES |  |  | JBS_MOT_001:2:O.Data.16 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_89405_ES |  |  | JBS_MOT_001:2:O.Data.17 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_89505_ES |  |  | JBS_MOT_001:2:O.Data.18 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_90301_ES |  |  | JBS_MOT_001:2:O.Data.19 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_91301_ES |  |  | JBS_MOT_001:2:O.Data.20 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_91351_ES |  |  | JBS_MOT_001:2:O.Data.21 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_91701_ES |  |  | JBS_MOT_001:2:O.Data.22 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_96303_ES |  |  | JBS_MOT_001:2:O.Data.23 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_96403_ES |  |  | JBS_MOT_001:2:O.Data.24 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_MIS_99301_ES |  |  | JBS_MOT_001:2:O.Data.25 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_30101_ES |  |  | JBS_MOT_001:1:O.Data.0 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_31101_ES |  |  | JBS_MOT_001:1:O.Data.1 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_32101_ES |  |  | JBS_MOT_001:1:O.Data.2 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_33101_ES |  |  | JBS_MOT_001:1:O.Data.3 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_33304_ES |  |  | JBS_MOT_001:1:O.Data.4 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_34101_ES |  |  | JBS_MOT_001:1:O.Data.5 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_34305_ES |  |  | JBS_MOT_001:1:O.Data.6 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_35101_ES |  |  | JBS_MOT_001:1:O.Data.7 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_35303_ES |  |  | JBS_MOT_001:1:O.Data.8 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_39101_ES |  |  | JBS_MOT_001:1:O.Data.9 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_39501_ES |  |  | JBS_MOT_001:1:O.Data.10 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_39801_ES |  |  | JBS_MOT_001:1:O.Data.11 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_40101_ES |  |  | JBS_MOT_001:1:O.Data.12 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_40303_ES |  |  | JBS_MOT_001:1:O.Data.13 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_41101_ES |  |  | JBS_MOT_001:1:O.Data.14 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_41304_ES |  |  | JBS_MOT_001:1:O.Data.15 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_42101_ES |  |  | JBS_MOT_001:1:O.Data.16 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_42303_ES |  |  | JBS_MOT_001:1:O.Data.17 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_86302_ES |  |  | JBS_MOT_001:1:O.Data.18 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_87302_ES |  |  | JBS_MOT_001:1:O.Data.19 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_88302_ES |  |  | JBS_MOT_001:1:O.Data.20 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_89105_ES |  |  | JBS_MOT_001:1:O.Data.21 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_89254_ES |  |  | JBS_MOT_001:1:O.Data.22 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_89605_ES |  |  | JBS_MOT_001:1:O.Data.23 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_89705_ES |  |  | JBS_MOT_001:1:O.Data.24 | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Digital_OUT | O_SIC_89805_ES |  |  | JBS_MOT_001:1:O.Data.25 | (RADIX := Decimal, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EP_Control | CM_SF_PC_BLK01_SIS01_02 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | ExternalComms | AOI_PC_BLK01_XIS_31024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_31041 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_31077 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_31078 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_32002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_33010 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_33011 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_35008 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39008 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39031 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39033 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39157 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39207 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_39435 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_40308 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_47505 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_80012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_82015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_83013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_84002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_85017 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_89554 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_99002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_99004 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_99302 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_BLK01_XIS_99501 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_82013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_83001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_84013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_85013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_86013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_87012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_LUL01_XIS_88012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_30003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_30024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_30027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_31019 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_31029 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_31053 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_31301 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_32010 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_32012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_32021 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_32306 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_33014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_33015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_33034 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_33040 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_33307 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_34013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_34024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_34027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_34030 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_34307 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_35001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_35003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_35004 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_35035 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_35047 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_39427 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_39727 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_40030 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_40201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_41020 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_41201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_42027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_42201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_80018 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_82001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_83016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_84016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_85016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_86009 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_86016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_86201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_87003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_87014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_87201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_88014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_88015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_88201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_90001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_91001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_91201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_91501 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_91506 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_91601 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_96201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_MFG01_XIS_96209 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_30003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_30024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_30027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31019 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31029 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31041 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31053 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31077 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31078 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_31301 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_32002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_32010 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_32012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_32021 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_32306 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33010 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33011 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33034 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33040 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_33307 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_34013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_34024 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_34027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_34030 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_34307 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35004 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35008 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35035 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_35047 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39008 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39031 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39033 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39157 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39207 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39358 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39427 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39435 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_39727 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_40030 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_40201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_40308 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_41020 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_41201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_42027 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_42201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_47505 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_80012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_80018 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_82001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_82013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_82015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_83001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_83013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_83016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_84002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_84013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_84016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_85013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_85016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_85017 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_86009 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_86013 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_86016 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_86201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_87003 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_87012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_87014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_87201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_88012 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_88014 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_88015 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_88201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_89554 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_90001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91001 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91005 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91501 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91506 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_91601 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_96201 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_96209 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_99002 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_99004 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_99302 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | AOI_PC_XIS_99501 |  | PC_Receive_V2W_V1 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_pc_BLK01_SIS01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_BLK01_SIS01_01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_BLK01_SIS01_02 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_pc_LUL01_SIS01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_LUL01_SIS01_01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_pc_MFG01_SIS01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_MFG01_SIS01_01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_MFG01_SIS01_02 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_MFG01_SIS01_03 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | ExternalComms | CM_SF_PC_MFG01_SIS01_04 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | IndexLooping | AGIT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | AGIT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | AIN_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AIN_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AIN_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AIN_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOD_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOD_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOD_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOD_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOUT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOUT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOUT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | AOUT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DI_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DI_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DI_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DI_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DOUT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DOUT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DOUT_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | DOUT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | EM_ADDPOT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_ADDPOT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_AGIT_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | EM_CONT_DLY_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_CONT_DLY_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_DLY_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_DLY_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_DLY_SCALE_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_DLY_SCALE_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | EM_HOLD_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_HOLD_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_INERT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_INERT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PREWEIGH_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PREWEIGH_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PROMPT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PROMPT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PRS_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_PRS_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_QC_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_QC_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_RECIRC_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_RECIRC_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_RECIRC_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | EM_RSC_MGR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_RSC_MGR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_RSC_MGR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | EM_STATUS_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_STATUS_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_TEMPJK_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_TEMPJK_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_TEMPVC_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_TEMPVC_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_VENT_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EM_VENT_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EX_REQ_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EX_REQ_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | EX_REQ_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | IND560_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | IND560_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | IND560_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | IND560_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | M2S_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | M2S_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | M2S_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | M2S_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MDG_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MDG_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MDG_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MDG_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MM_CIR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MM_CIR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MM_CIR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MM_CIR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MP4_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MP4_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MP4_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MP4_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MPG_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | MPG_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | MPG_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | MPG_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | pc_V2W_Array_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | pc_V2W_Array_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | pc_V2W_Array_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | pc_V2W_Array_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | PMR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | PMR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | PMR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | PMR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SF_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | SF_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | SF_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SF_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SZ_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SZ_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SZ_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | SZ_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2WHR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | V2WHR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | V2WHR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | V2WHR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | V2WR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2WR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2WR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2WR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2W_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2W_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2W_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V2W_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3D_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3D_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3D_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3D_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3W_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3W_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3W_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | V3W_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VDB_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | VDB_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | VDB_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VDB_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD2S_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD2S_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD2S_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD2S_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD755_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | VFD755_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | IndexLooping | VFD755_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFD755_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFDCH_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFDCH_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFDCH_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VFDCH_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VPR_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VPR_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VPR_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VPR_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VSL_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VSL_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VSL_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | VSL_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSGE_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | WSGE_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | IndexLooping | WSGE_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSGE_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSP_LoopCnt |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSP_LoopEnable |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSP_Offset |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TAG | IndexLooping | WSP_Size |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read Only)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Modules | CM_EX_REQ_PC_BLK01_SIS01_01 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_BLK01_SIS01_02 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_LUL01_SIS01_01 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_MFG01_SIS01_01 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_MFG01_SIS01_02 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_MFG01_SIS01_03 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | Modules | CM_EX_REQ_PC_MFG01_SIS01_04 |  | EX_REQ_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SafetyZones | CM_SZ_EMModules |  | CM_SZONE_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | SafetyZones | CM_SZ_SystemWide |  | CM_SZONE_V3 |  | (Constant := false, ExternalAccess := Read Only)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SolenoidDevices | CM_XS_98500 |  | CM_DOUT_V3 |  | (Constant := false, ExternalAccess := Read Only)
ALIAS | SolenoidDevices | O_XS_98500 |  |  | JBS_Z7_001:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SystemFaults | ADDPOT_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | ADDPOT_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | AGIT_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | AGIT_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | ALARM_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | CM_SF_HMI_COMM_SIS01 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | CM_SF_T981 |  | CM_SF_V3 |  | (Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | COFEED_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | COFEED_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | CONT_DLY_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | CONT_DLY_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | DLY_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | DLY_ONS |  | BOOL[544] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | DLY_SCALE_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | DLY_SCALE_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | HOLD_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | HOLD_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | INERT_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | INERT_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
ALIAS | SystemFaults | I_SF_HMI_COMM_SIS01 |  |  | GlobalComm.tmrHeartBeatMonitor.DN | (RADIX := Decimal, ExternalAccess := Read Only)
TAG | SystemFaults | PREWEIGH_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | PREWEIGH_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | PROMPT_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | PROMPT_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | PRS_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | PRS_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | QC_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | QC_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | RECIRC_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | RECIRC_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | STATUS_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | STATUS_ONS |  | BOOL[32] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | TEMPJK_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | TEMPJK_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | TEMPVC_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | TEMPVC_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | VENT_LOOP |  | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TAG | SystemFaults | VENT_ONS |  | BOOL[64] |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | System_Status | DelayReset |  | TIMER |  | (Constant := false, ExternalAccess := Read/Write)
TAG | System_Status | ONS |  | BOOL |  | (RADIX := Decimal, Constant := false, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | UsingList | MaxModules | Maximum Number Of Allowed Modules | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | UsingList | MaxModulesOffset | Max Modules With Zero Offset | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | UsingList | MaxUsers | Maximum Configured Users | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | UsingList | MaxUsersOffset | Max Users With Zero Index | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | UsingList | ModuleLoopIndex | Module Looping Index | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TAG | UsingList | UsersLoopIndex | Users Loop Index | DINT |  | (RADIX := Decimal, Constant := false, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | Valves | CM_XIS_30003 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_30024 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_30027 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31019 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31024 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31029 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31041 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31053 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31073 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31077 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31078 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_31301 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_32002 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_32010 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_32012 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_32021 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_32306 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33010 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33011 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33014 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33015 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33034 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33040 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_33307 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34004 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34024 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34027 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34030 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_34307 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35001 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35003 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35004 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35008 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35035 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_35047 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39008 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39031 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39033 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39157 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39207 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39358 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39427 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39435 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39441 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39442 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39443 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39727 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39741 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39742 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_39743 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_40030 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_40201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_40308 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_41020 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_41201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_42027 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_42201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_47505 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_80012 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_80018 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82001 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82015 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82041 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82042 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_82043 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83001 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83016 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83041 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83042 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_83043 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84002 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84016 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84041 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84042 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_84043 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85016 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85017 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85041 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85042 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_85043 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_86009 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_86013 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_86016 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_86201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_87003 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_87012 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_87014 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_87201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_88012 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_88014 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_88015 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_88201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_89554 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_90001 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_91001 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_91201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_91501 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_91506 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_91601 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_96201 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_96202 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_96209 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_99002 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_99004 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_99302 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
TAG | Valves | CM_XIS_99501 |  | CM_V2W_V3 |  | (Constant := false, ExternalAccess := Read Only)
ALIAS | Valves | FLT_I_XIS_30003_XSC |  |  | JBS_Z6_041:12:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_30003_XSO |  |  | JBS_Z6_041:12:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_30024_XSC |  |  | JBS_Z6_041:12:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_30024_XSO |  |  | JBS_Z6_041:12:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_30027_XSC |  |  | JBS_Z6_061:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_30027_XSO |  |  | JBS_Z6_061:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31019_XSC |  |  | JBS_Z6_041:12:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31019_XSO |  |  | JBS_Z6_041:12:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31024_XSC |  |  | JBS_Z6_041:12:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31024_XSO |  |  | JBS_Z6_041:12:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31029_XSC |  |  | JBS_Z6_031:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31029_XSO |  |  | JBS_Z6_031:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31041_XSC |  |  | JBS_Z6_021:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31041_XSO |  |  | JBS_Z6_021:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31053_XSC |  |  | JBS_Z6_041:13:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31053_XSO |  |  | JBS_Z6_041:13:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31073_XSC |  |  | JBS_Z6_041:13:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31073_XSO |  |  | JBS_Z6_041:13:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31077_XSC |  |  | JBS_Z6_021:6:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31077_XSO |  |  | JBS_Z6_021:6:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31078_XSC |  |  | JBS_Z6_021:6:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31078_XSO |  |  | JBS_Z6_021:6:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31301_XSC |  |  | JBS_Z6_041:13:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_31301_XSO |  |  | JBS_Z6_041:13:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32002_XSC |  |  | JBS_Z6_031:8:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32002_XSO |  |  | JBS_Z6_031:8:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32010_XSC |  |  | JBS_Z6_001:12:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32010_XSO |  |  | JBS_Z6_001:12:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32012_XSC |  |  | JBS_Z6_001:12:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32012_XSO |  |  | JBS_Z6_001:12:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32021_XSC |  |  | JBS_Z6_031:8:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32021_XSO |  |  | JBS_Z6_031:8:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32306_XSC |  |  | JBS_Z6_001:12:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_32306_XSO |  |  | JBS_Z6_001:12:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33010_XSC |  |  | JBS_Z6_031:8:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33010_XSO |  |  | JBS_Z6_031:8:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33011_XSC |  |  | JBS_Z6_031:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33011_XSO |  |  | JBS_Z6_031:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33014_XSC |  |  | JBS_Z6_031:9:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33014_XSO |  |  | JBS_Z6_031:9:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33015_XSC |  |  | JBS_Z6_021:6:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33015_XSO |  |  | JBS_Z6_021:6:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33034_XSC |  |  | JBS_Z6_001:12:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33034_XSO |  |  | JBS_Z6_001:12:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33040_XSC |  |  | JBS_Z6_001:13:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33040_XSO |  |  | JBS_Z6_001:13:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33307_XSC |  |  | JBS_Z6_001:13:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_33307_XSO |  |  | JBS_Z6_001:13:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34004_XSC |  |  | JBS_Z6_001:13:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34004_XSO |  |  | JBS_Z6_001:13:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34013_XSC |  |  | JBS_Z6_001:13:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34013_XSO |  |  | JBS_Z6_001:13:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34024_XSC |  |  | JBS_Z6_031:9:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34024_XSO |  |  | JBS_Z6_031:9:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34027_XSC |  |  | JBS_Z6_001:14:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34027_XSO |  |  | JBS_Z6_001:14:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34030_XSC |  |  | JBS_Z6_021:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34030_XSO |  |  | JBS_Z6_021:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34307_XSC |  |  | JBS_Z6_001:14:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_34307_XSO |  |  | JBS_Z6_001:14:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35001_XSC |  |  | JBS_Z6_001:14:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35001_XSO |  |  | JBS_Z6_001:14:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35003_XSC |  |  | JBS_Z6_031:9:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35003_XSO |  |  | JBS_Z6_031:9:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35004_XSC |  |  | JBS_Z6_001:14:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35004_XSO |  |  | JBS_Z6_001:14:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35008_XSC |  |  | JBS_Z6_031:10:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35008_XSO |  |  | JBS_Z6_031:10:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35035_XSC |  |  | JBS_Z6_001:15:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35035_XSO |  |  | JBS_Z6_001:15:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35047_XSC |  |  | JBS_Z6_021:7:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_35047_XSO |  |  | JBS_Z6_021:7:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39008_XSC |  |  | JBS_Z6_041:13:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39008_XSO |  |  | JBS_Z6_041:13:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39031_XSC |  |  | JBS_Z6_031:10:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39031_XSO |  |  | JBS_Z6_031:10:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39033_XSC |  |  | JBS_Z6_021:7:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39033_XSO |  |  | JBS_Z6_021:7:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39157_XSC |  |  | JBS_Z6_031:10:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39157_XSO |  |  | JBS_Z6_031:10:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39207_XSC |  |  | JBS_Z6_021:7:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39207_XSO |  |  | JBS_Z6_021:7:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39358_XSC |  |  | JBS_Z6_041:14:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39358_XSO |  |  | JBS_Z6_041:14:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39427_XSC |  |  | JBS_Z6_041:14:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39427_XSO |  |  | JBS_Z6_041:14:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39435_XSC |  |  | JBS_Z6_041:15:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39435_XSO |  |  | JBS_Z6_041:15:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39441_XSC |  |  | JBS_Z6_041:16:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39442_XSC |  |  | JBS_Z6_041:14:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39442_XSO |  |  | JBS_Z6_041:14:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39443_XSC |  |  | JBS_Z6_041:14:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39443_XSO |  |  | JBS_Z6_041:14:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39727_XSC |  |  | JBS_Z6_041:15:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39727_XSO |  |  | JBS_Z6_041:15:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39741_XSC |  |  | JBS_Z6_041:16:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39742_XSC |  |  | JBS_Z6_041:15:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39742_XSO |  |  | JBS_Z6_041:15:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39743_XSC |  |  | JBS_Z6_041:15:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_39743_XSO |  |  | JBS_Z6_041:15:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40030_XSC |  |  | JBS_Z4_021:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40030_XSO |  |  | JBS_Z4_021:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40201_XSC |  |  | JBS_Z6_001:15:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40201_XSO |  |  | JBS_Z6_001:15:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40308_XSC |  |  | JBS_Z4_021:4:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_40308_XSO |  |  | JBS_Z4_021:4:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_41020_XSC |  |  | JBS_Z4_021:4:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_41020_XSO |  |  | JBS_Z4_021:4:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_41201_XSC |  |  | JBS_Z6_001:15:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_41201_XSO |  |  | JBS_Z6_001:15:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_42027_XSC |  |  | JBS_Z4_021:4:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_42027_XSO |  |  | JBS_Z4_021:4:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_42201_XSC |  |  | JBS_Z6_001:15:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_42201_XSO |  |  | JBS_Z6_001:15:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_47505_XSC |  |  | JBS_Z6_001:16:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_47505_XSO |  |  | JBS_Z6_001:16:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_80012_XSC |  |  | JBS_Z2_001:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_80012_XSO |  |  | JBS_Z2_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_80018_XSC |  |  | JBS_Z2_001:3:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_80018_XSO |  |  | JBS_Z2_001:3:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82001_XSC |  |  | JBS_Z2_021:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82001_XSO |  |  | JBS_Z2_021:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82013_XSC |  |  | JBS_Z2_021:6:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82013_XSO |  |  | JBS_Z2_021:6:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82015_XSC |  |  | JBS_Z2_002:12:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82015_XSO |  |  | JBS_Z2_002:12:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82041_XSC |  |  | JBS_Z2_002:15:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82042_XSC |  |  | JBS_Z2_002:12:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82042_XSO |  |  | JBS_Z2_002:12:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82043_XSC |  |  | JBS_Z2_002:12:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_82043_XSO |  |  | JBS_Z2_002:12:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83001_XSC |  |  | JBS_Z2_021:6:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83001_XSO |  |  | JBS_Z2_021:6:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83013_XSC |  |  | JBS_Z2_002:12:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83013_XSO |  |  | JBS_Z2_002:12:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83016_XSC |  |  | JBS_Z2_021:6:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83016_XSO |  |  | JBS_Z2_021:6:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83041_XSC |  |  | JBS_Z2_002:15:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83042_XSC |  |  | JBS_Z2_002:13:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83042_XSO |  |  | JBS_Z2_002:13:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83043_XSC |  |  | JBS_Z2_002:13:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_83043_XSO |  |  | JBS_Z2_002:13:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84002_XSC |  |  | JBS_Z2_002:13:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84002_XSO |  |  | JBS_Z2_002:13:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84013_XSC |  |  | JBS_Z2_021:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84013_XSO |  |  | JBS_Z2_021:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84016_XSC |  |  | JBS_Z2_021:7:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84016_XSO |  |  | JBS_Z2_021:7:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84041_XSC |  |  | JBS_Z2_002:15:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84042_XSC |  |  | JBS_Z2_002:13:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84042_XSO |  |  | JBS_Z2_002:13:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84043_XSC |  |  | JBS_Z2_002:14:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_84043_XSO |  |  | JBS_Z2_002:14:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85013_XSC |  |  | JBS_Z2_021:7:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85013_XSO |  |  | JBS_Z2_021:7:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85016_XSC |  |  | JBS_Z2_021:7:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85016_XSO |  |  | JBS_Z2_021:7:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85017_XSC |  |  | JBS_Z2_002:14:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85017_XSO |  |  | JBS_Z2_002:14:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85041_XSC |  |  | JBS_Z2_002:15:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85042_XSC |  |  | JBS_Z2_002:14:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85042_XSO |  |  | JBS_Z2_002:14:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85043_XSC |  |  | JBS_Z2_002:14:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_85043_XSO |  |  | JBS_Z2_002:14:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86009_XSC |  |  | JBS_Z5_001:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86009_XSO |  |  | JBS_Z5_001:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86013_XSC |  |  | JBS_Z5_001:8:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86013_XSO |  |  | JBS_Z5_001:8:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86016_XSC |  |  | JBS_Z5_001:8:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86016_XSO |  |  | JBS_Z5_001:8:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86201_XSC |  |  | JBS_Z5_001:8:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_86201_XSO |  |  | JBS_Z5_001:8:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87003_XSC |  |  | JBS_Z5_001:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87003_XSO |  |  | JBS_Z5_001:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87012_XSC |  |  | JBS_Z5_001:9:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87012_XSO |  |  | JBS_Z5_001:9:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87014_XSC |  |  | JBS_Z5_001:9:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87014_XSO |  |  | JBS_Z5_001:9:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87201_XSC |  |  | JBS_Z5_001:9:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_87201_XSO |  |  | JBS_Z5_001:9:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88012_XSC |  |  | JBS_Z5_001:10:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88012_XSO |  |  | JBS_Z5_001:10:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88014_XSC |  |  | JBS_Z5_001:10:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88014_XSO |  |  | JBS_Z5_001:10:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88015_XSC |  |  | JBS_Z5_001:10:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88015_XSO |  |  | JBS_Z5_001:10:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88201_XSC |  |  | JBS_Z5_001:10:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_88201_XSO |  |  | JBS_Z5_001:10:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_89554_XSC |  |  | JBS_Z6_041:16:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_89554_XSO |  |  | JBS_Z6_041:16:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_90001_XSC |  |  | JBS_Z7_001:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_90001_XSO |  |  | JBS_Z7_001:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91001_XSC |  |  | JBS_Z7_001:5:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91001_XSO |  |  | JBS_Z7_001:5:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91201_XSC |  |  | JBS_Z7_001:5:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91201_XSO |  |  | JBS_Z7_001:5:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91501_XSC |  |  | JBS_Z7_001:5:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91501_XSO |  |  | JBS_Z7_001:5:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91506_XSC |  |  | JBS_Z7_001:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91506_XSO |  |  | JBS_Z7_001:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91601_XSC |  |  | JBS_Z7_001:6:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_91601_XSO |  |  | JBS_Z7_001:6:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96201_XSC |  |  | JBS_Z1_001:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96201_XSO |  |  | JBS_Z1_001:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96202_XSC |  |  | JBS_Z1_001:4:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96202_XSO |  |  | JBS_Z1_001:4:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96209_XSC |  |  | JBS_Z1_001:4:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_96209_XSO |  |  | JBS_Z1_001:4:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99002_XSC |  |  | JBS_Z6_001:16:I.Pt04.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99002_XSO |  |  | JBS_Z6_001:16:I.Pt03.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99004_XSC |  |  | JBS_Z6_001:16:I.Pt06.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99004_XSO |  |  | JBS_Z6_001:16:I.Pt05.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99302_XSC |  |  | JBS_Z6_001:16:I.Pt08.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99302_XSO |  |  | JBS_Z6_001:16:I.Pt07.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99501_XSC |  |  | JBS_Z6_001:17:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_I_XIS_99501_XSO |  |  | JBS_Z6_001:17:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_30003_XS |  |  | JBS_Z6_041:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_30024_XS |  |  | JBS_Z6_041:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_30027_XS |  |  | JBS_Z6_061:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31019_XS |  |  | JBS_Z6_041:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31024_XS |  |  | JBS_Z6_041:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31029_XS |  |  | JBS_Z6_031:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31041_XS |  |  | JBS_Z6_021:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31053_XS |  |  | JBS_Z6_041:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31073_XS |  |  | JBS_Z6_041:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31077_XS |  |  | JBS_Z6_021:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31078_XS |  |  | JBS_Z6_021:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_31301_XS |  |  | JBS_Z6_041:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_32002_XS |  |  | JBS_Z6_031:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_32010_XS |  |  | JBS_Z6_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_32012_XS |  |  | JBS_Z6_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_32021_XS |  |  | JBS_Z6_031:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_32306_XS |  |  | JBS_Z6_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33010_XS |  |  | JBS_Z6_031:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33011_XS |  |  | JBS_Z6_031:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33014_XS |  |  | JBS_Z6_031:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33015_XS |  |  | JBS_Z6_021:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33034_XS |  |  | JBS_Z6_001:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33040_XS |  |  | JBS_Z6_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_33307_XS |  |  | JBS_Z6_001:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34004_XS |  |  | JBS_Z6_001:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34013_XS |  |  | JBS_Z6_001:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34024_XS |  |  | JBS_Z6_031:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34027_XS |  |  | JBS_Z6_001:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34030_XS |  |  | JBS_Z6_021:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_34307_XS |  |  | JBS_Z6_001:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35001_XS |  |  | JBS_Z6_001:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35003_XS |  |  | JBS_Z6_031:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35004_XS |  |  | JBS_Z6_001:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35008_XS |  |  | JBS_Z6_031:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35035_XS |  |  | JBS_Z6_001:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_35047_XS |  |  | JBS_Z6_021:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39008_XS |  |  | JBS_Z6_041:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39031_XS |  |  | JBS_Z6_031:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39033_XS |  |  | JBS_Z6_021:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39157_XS |  |  | JBS_Z6_031:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39207_XS |  |  | JBS_Z6_021:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39358_XS |  |  | JBS_Z6_041:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39427_XS |  |  | JBS_Z6_041:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39435_XS |  |  | JBS_Z6_041:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39442_XS1 |  |  | JBS_Z6_041:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39442_XS2 |  |  | JBS_Z6_041:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39443_XS1 |  |  | JBS_Z6_041:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39443_XS2 |  |  | JBS_Z6_041:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39727_XS |  |  | JBS_Z6_041:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39742_XS1 |  |  | JBS_Z6_041:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39742_XS2 |  |  | JBS_Z6_041:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39743_XS1 |  |  | JBS_Z6_041:10:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_39743_XS2 |  |  | JBS_Z6_041:10:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_40030_XS |  |  | JBS_Z4_021:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_40201_XS |  |  | JBS_Z6_001:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_40308_XS |  |  | JBS_Z4_021:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_41020_XS |  |  | JBS_Z4_021:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_41201_XS |  |  | JBS_Z6_001:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_42027_XS |  |  | JBS_Z4_021:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_42201_XS |  |  | JBS_Z6_001:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_47505_XS |  |  | JBS_Z6_001:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_80012_XS |  |  | JBS_Z2_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_80018_XS |  |  | JBS_Z2_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82001_XS |  |  | JBS_Z2_021:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82013_XS |  |  | JBS_Z2_021:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82015_XS |  |  | JBS_Z2_002:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82042_XS1 |  |  | JBS_Z2_002:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82042_XS2 |  |  | JBS_Z2_002:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82043_XS1 |  |  | JBS_Z2_002:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_82043_XS2 |  |  | JBS_Z2_002:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83001_XS |  |  | JBS_Z2_021:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83013_XS |  |  | JBS_Z2_002:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83016_XS |  |  | JBS_Z2_021:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83042_XS1 |  |  | JBS_Z2_002:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83042_XS2 |  |  | JBS_Z2_002:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83043_XS1 |  |  | JBS_Z2_002:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_83043_XS2 |  |  | JBS_Z2_002:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84002_XS |  |  | JBS_Z2_002:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84013_XS |  |  | JBS_Z2_021:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84016_XS |  |  | JBS_Z2_021:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84042_XS1 |  |  | JBS_Z2_002:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84042_XS2 |  |  | JBS_Z2_002:7:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84043_XS1 |  |  | JBS_Z2_002:7:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_84043_XS2 |  |  | JBS_Z2_002:8:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85013_XS |  |  | JBS_Z2_021:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85016_XS |  |  | JBS_Z2_021:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85017_XS |  |  | JBS_Z2_002:8:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85042_XS1 |  |  | JBS_Z2_002:9:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85042_XS2 |  |  | JBS_Z2_002:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85043_XS1 |  |  | JBS_Z2_002:10:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_85043_XS2 |  |  | JBS_Z2_002:10:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_86009_XS |  |  | JBS_Z5_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_86013_XS |  |  | JBS_Z5_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_86016_XS |  |  | JBS_Z5_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_86201_XS |  |  | JBS_Z5_001:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_87003_XS |  |  | JBS_Z5_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_87012_XS |  |  | JBS_Z5_001:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_87014_XS |  |  | JBS_Z5_001:4:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_87201_XS |  |  | JBS_Z5_001:4:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_88012_XS |  |  | JBS_Z5_001:5:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_88014_XS |  |  | JBS_Z5_001:5:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_88015_XS |  |  | JBS_Z5_001:6:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_88201_XS |  |  | JBS_Z5_001:6:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_89554_XS |  |  | JBS_Z6_041:11:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_90001_XS |  |  | JBS_Z7_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_91001_XS |  |  | JBS_Z7_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_91201_XS |  |  | JBS_Z7_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_91501_XS |  |  | JBS_Z7_001:2:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_91506_XS |  |  | JBS_Z7_001:3:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_91601_XS |  |  | JBS_Z7_001:3:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_96201_XS |  |  | JBS_Z1_001:1:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_96202_XS |  |  | JBS_Z1_001:1:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_96209_XS |  |  | JBS_Z1_001:2:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_99002_XS |  |  | JBS_Z6_001:9:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_99004_XS |  |  | JBS_Z6_001:10:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_99302_XS |  |  | JBS_Z6_001:10:I.Pt02.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | FLT_O_XIS_99501_XS |  |  | JBS_Z6_001:11:I.Pt01.Fault | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30003_XSC |  |  | JBS_Z6_041:12:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30003_XSO |  |  | JBS_Z6_041:12:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30024_XSC |  |  | JBS_Z6_041:12:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30024_XSO |  |  | JBS_Z6_041:12:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30027_XSC |  |  | JBS_Z6_061:3:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_30027_XSO |  |  | JBS_Z6_061:3:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31019_XSC |  |  | JBS_Z6_041:12:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31019_XSO |  |  | JBS_Z6_041:12:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31024_XSC |  |  | JBS_Z6_041:12:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31024_XSO |  |  | JBS_Z6_041:12:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31029_XSC |  |  | JBS_Z6_031:8:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31029_XSO |  |  | JBS_Z6_031:8:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31041_XSC |  |  | JBS_Z6_021:6:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31041_XSO |  |  | JBS_Z6_021:6:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31053_XSC |  |  | JBS_Z6_041:13:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31053_XSO |  |  | JBS_Z6_041:13:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31073_XSC |  |  | JBS_Z6_041:13:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31073_XSO |  |  | JBS_Z6_041:13:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31077_XSC |  |  | JBS_Z6_021:6:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31077_XSO |  |  | JBS_Z6_021:6:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31078_XSC |  |  | JBS_Z6_021:6:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31078_XSO |  |  | JBS_Z6_021:6:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31301_XSC |  |  | JBS_Z6_041:13:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_31301_XSO |  |  | JBS_Z6_041:13:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32002_XSC |  |  | JBS_Z6_031:8:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32002_XSO |  |  | JBS_Z6_031:8:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32010_XSC |  |  | JBS_Z6_001:12:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32010_XSO |  |  | JBS_Z6_001:12:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32012_XSC |  |  | JBS_Z6_001:12:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32012_XSO |  |  | JBS_Z6_001:12:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32021_XSC |  |  | JBS_Z6_031:8:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32021_XSO |  |  | JBS_Z6_031:8:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32306_XSC |  |  | JBS_Z6_001:12:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_32306_XSO |  |  | JBS_Z6_001:12:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33010_XSC |  |  | JBS_Z6_031:8:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33010_XSO |  |  | JBS_Z6_031:8:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33011_XSC |  |  | JBS_Z6_031:9:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33011_XSO |  |  | JBS_Z6_031:9:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33014_XSC |  |  | JBS_Z6_031:9:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33014_XSO |  |  | JBS_Z6_031:9:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33015_XSC |  |  | JBS_Z6_021:6:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33015_XSO |  |  | JBS_Z6_021:6:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33034_XSC |  |  | JBS_Z6_001:12:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33034_XSO |  |  | JBS_Z6_001:12:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33040_XSC |  |  | JBS_Z6_001:13:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33040_XSO |  |  | JBS_Z6_001:13:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33307_XSC |  |  | JBS_Z6_001:13:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_33307_XSO |  |  | JBS_Z6_001:13:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34004_XSC |  |  | JBS_Z6_001:13:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34004_XSO |  |  | JBS_Z6_001:13:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34013_XSC |  |  | JBS_Z6_001:13:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34013_XSO |  |  | JBS_Z6_001:13:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34024_XSC |  |  | JBS_Z6_031:9:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34024_XSO |  |  | JBS_Z6_031:9:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34027_XSC |  |  | JBS_Z6_001:14:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34027_XSO |  |  | JBS_Z6_001:14:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34030_XSC |  |  | JBS_Z6_021:7:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34030_XSO |  |  | JBS_Z6_021:7:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34307_XSC |  |  | JBS_Z6_001:14:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_34307_XSO |  |  | JBS_Z6_001:14:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35001_XSC |  |  | JBS_Z6_001:14:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35001_XSO |  |  | JBS_Z6_001:14:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35003_XSC |  |  | JBS_Z6_031:9:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35003_XSO |  |  | JBS_Z6_031:9:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35004_XSC |  |  | JBS_Z6_001:14:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35004_XSO |  |  | JBS_Z6_001:14:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35008_XSC |  |  | JBS_Z6_031:10:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35008_XSO |  |  | JBS_Z6_031:10:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35035_XSC |  |  | JBS_Z6_001:15:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35035_XSO |  |  | JBS_Z6_001:15:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35047_XSC |  |  | JBS_Z6_021:7:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_35047_XSO |  |  | JBS_Z6_021:7:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39008_XSC |  |  | JBS_Z6_041:13:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39008_XSO |  |  | JBS_Z6_041:13:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39031_XSC |  |  | JBS_Z6_031:10:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39031_XSO |  |  | JBS_Z6_031:10:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39033_XSC |  |  | JBS_Z6_021:7:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39033_XSO |  |  | JBS_Z6_021:7:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39157_XSC |  |  | JBS_Z6_031:10:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39157_XSO |  |  | JBS_Z6_031:10:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39207_XSC |  |  | JBS_Z6_021:7:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39207_XSO |  |  | JBS_Z6_021:7:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39358_XSC |  |  | JBS_Z6_041:14:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39358_XSO |  |  | JBS_Z6_041:14:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39427_XSC |  |  | JBS_Z6_041:14:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39427_XSO |  |  | JBS_Z6_041:14:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39435_XSC |  |  | JBS_Z6_041:15:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39435_XSO |  |  | JBS_Z6_041:15:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39441_XSC |  |  | JBS_Z6_041:16:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39442_XSC |  |  | JBS_Z6_041:14:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39442_XSO |  |  | JBS_Z6_041:14:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39443_XSC |  |  | JBS_Z6_041:14:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39443_XSO |  |  | JBS_Z6_041:14:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39727_XSC |  |  | JBS_Z6_041:15:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39727_XSO |  |  | JBS_Z6_041:15:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39741_XSC |  |  | JBS_Z6_041:16:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39742_XSC |  |  | JBS_Z6_041:15:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39742_XSO |  |  | JBS_Z6_041:15:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39743_XSC |  |  | JBS_Z6_041:15:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_39743_XSO |  |  | JBS_Z6_041:15:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40030_XSC |  |  | JBS_Z4_021:4:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40030_XSO |  |  | JBS_Z4_021:4:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40201_XSC |  |  | JBS_Z6_001:15:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40201_XSO |  |  | JBS_Z6_001:15:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40308_XSC |  |  | JBS_Z4_021:4:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_40308_XSO |  |  | JBS_Z4_021:4:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_41020_XSC |  |  | JBS_Z4_021:4:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_41020_XSO |  |  | JBS_Z4_021:4:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_41201_XSC |  |  | JBS_Z6_001:15:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_41201_XSO |  |  | JBS_Z6_001:15:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_42027_XSC |  |  | JBS_Z4_021:4:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_42027_XSO |  |  | JBS_Z4_021:4:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_42201_XSC |  |  | JBS_Z6_001:15:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_42201_XSO |  |  | JBS_Z6_001:15:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_47505_XSC |  |  | JBS_Z6_001:16:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_47505_XSO |  |  | JBS_Z6_001:16:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_80012_XSC |  |  | JBS_Z2_001:3:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_80012_XSO |  |  | JBS_Z2_001:3:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_80018_XSC |  |  | JBS_Z2_001:3:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_80018_XSO |  |  | JBS_Z2_001:3:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82001_XSC |  |  | JBS_Z2_021:6:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82001_XSO |  |  | JBS_Z2_021:6:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82013_XSC |  |  | JBS_Z2_021:6:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82013_XSO |  |  | JBS_Z2_021:6:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82015_XSC |  |  | JBS_Z2_002:12:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82015_XSO |  |  | JBS_Z2_002:12:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82041_XSC |  |  | JBS_Z2_002:15:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82042_XSC |  |  | JBS_Z2_002:12:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82042_XSO |  |  | JBS_Z2_002:12:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82043_XSC |  |  | JBS_Z2_002:12:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_82043_XSO |  |  | JBS_Z2_002:12:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83001_XSC |  |  | JBS_Z2_021:6:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83001_XSO |  |  | JBS_Z2_021:6:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83013_XSC |  |  | JBS_Z2_002:12:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83013_XSO |  |  | JBS_Z2_002:12:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83016_XSC |  |  | JBS_Z2_021:6:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83016_XSO |  |  | JBS_Z2_021:6:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83041_XSC |  |  | JBS_Z2_002:15:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83042_XSC |  |  | JBS_Z2_002:13:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83042_XSO |  |  | JBS_Z2_002:13:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83043_XSC |  |  | JBS_Z2_002:13:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_83043_XSO |  |  | JBS_Z2_002:13:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84002_XSC |  |  | JBS_Z2_002:13:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84002_XSO |  |  | JBS_Z2_002:13:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84013_XSC |  |  | JBS_Z2_021:7:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84013_XSO |  |  | JBS_Z2_021:7:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84016_XSC |  |  | JBS_Z2_021:7:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84016_XSO |  |  | JBS_Z2_021:7:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84041_XSC |  |  | JBS_Z2_002:15:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84042_XSC |  |  | JBS_Z2_002:13:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84042_XSO |  |  | JBS_Z2_002:13:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84043_XSC |  |  | JBS_Z2_002:14:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_84043_XSO |  |  | JBS_Z2_002:14:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85013_XSC |  |  | JBS_Z2_021:7:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85013_XSO |  |  | JBS_Z2_021:7:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85016_XSC |  |  | JBS_Z2_021:7:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85016_XSO |  |  | JBS_Z2_021:7:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85017_XSC |  |  | JBS_Z2_002:14:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85017_XSO |  |  | JBS_Z2_002:14:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85041_XSC |  |  | JBS_Z2_002:15:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85042_XSC |  |  | JBS_Z2_002:14:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85042_XSO |  |  | JBS_Z2_002:14:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85043_XSC |  |  | JBS_Z2_002:14:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_85043_XSO |  |  | JBS_Z2_002:14:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86009_XSC |  |  | JBS_Z5_001:8:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86009_XSO |  |  | JBS_Z5_001:8:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86013_XSC |  |  | JBS_Z5_001:8:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86013_XSO |  |  | JBS_Z5_001:8:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86016_XSC |  |  | JBS_Z5_001:8:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86016_XSO |  |  | JBS_Z5_001:8:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86201_XSC |  |  | JBS_Z5_001:8:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_86201_XSO |  |  | JBS_Z5_001:8:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87003_XSC |  |  | JBS_Z5_001:9:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87003_XSO |  |  | JBS_Z5_001:9:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87012_XSC |  |  | JBS_Z5_001:9:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87012_XSO |  |  | JBS_Z5_001:9:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87014_XSC |  |  | JBS_Z5_001:9:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87014_XSO |  |  | JBS_Z5_001:9:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87201_XSC |  |  | JBS_Z5_001:9:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_87201_XSO |  |  | JBS_Z5_001:9:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88012_XSC |  |  | JBS_Z5_001:10:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88012_XSO |  |  | JBS_Z5_001:10:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88014_XSC |  |  | JBS_Z5_001:10:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88014_XSO |  |  | JBS_Z5_001:10:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88015_XSC |  |  | JBS_Z5_001:10:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88015_XSO |  |  | JBS_Z5_001:10:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88201_XSC |  |  | JBS_Z5_001:10:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_88201_XSO |  |  | JBS_Z5_001:10:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_89554_XSC |  |  | JBS_Z6_041:16:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_89554_XSO |  |  | JBS_Z6_041:16:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_90001_XSC |  |  | JBS_Z7_001:5:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_90001_XSO |  |  | JBS_Z7_001:5:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91001_XSC |  |  | JBS_Z7_001:5:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91001_XSO |  |  | JBS_Z7_001:5:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91201_XSC |  |  | JBS_Z7_001:5:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91201_XSO |  |  | JBS_Z7_001:5:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91501_XSC |  |  | JBS_Z7_001:5:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91501_XSO |  |  | JBS_Z7_001:5:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91506_XSC |  |  | JBS_Z7_001:6:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91506_XSO |  |  | JBS_Z7_001:6:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91601_XSC |  |  | JBS_Z7_001:6:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_91601_XSO |  |  | JBS_Z7_001:6:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96201_XSC |  |  | JBS_Z1_001:4:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96201_XSO |  |  | JBS_Z1_001:4:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96202_XSC |  |  | JBS_Z1_001:4:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96202_XSO |  |  | JBS_Z1_001:4:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96209_XSC |  |  | JBS_Z1_001:4:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_96209_XSO |  |  | JBS_Z1_001:4:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99002_XSC |  |  | JBS_Z6_001:16:I.Pt04.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99002_XSO |  |  | JBS_Z6_001:16:I.Pt03.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99004_XSC |  |  | JBS_Z6_001:16:I.Pt06.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99004_XSO |  |  | JBS_Z6_001:16:I.Pt05.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99302_XSC |  |  | JBS_Z6_001:16:I.Pt08.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99302_XSO |  |  | JBS_Z6_001:16:I.Pt07.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99501_XSC |  |  | JBS_Z6_001:17:I.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | I_XIS_99501_XSO |  |  | JBS_Z6_001:17:I.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_30003_XS |  |  | JBS_Z6_041:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_30024_XS |  |  | JBS_Z6_041:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_30027_XS |  |  | JBS_Z6_061:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31019_XS |  |  | JBS_Z6_041:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31024_XS |  |  | JBS_Z6_041:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31029_XS |  |  | JBS_Z6_031:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31041_XS |  |  | JBS_Z6_021:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31053_XS |  |  | JBS_Z6_041:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31073_XS |  |  | JBS_Z6_041:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31077_XS |  |  | JBS_Z6_021:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31078_XS |  |  | JBS_Z6_021:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_31301_XS |  |  | JBS_Z6_041:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_32002_XS |  |  | JBS_Z6_031:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_32010_XS |  |  | JBS_Z6_001:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_32012_XS |  |  | JBS_Z6_001:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_32021_XS |  |  | JBS_Z6_031:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_32306_XS |  |  | JBS_Z6_001:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33010_XS |  |  | JBS_Z6_031:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33011_XS |  |  | JBS_Z6_031:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33014_XS |  |  | JBS_Z6_031:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33015_XS |  |  | JBS_Z6_021:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33034_XS |  |  | JBS_Z6_001:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33040_XS |  |  | JBS_Z6_001:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_33307_XS |  |  | JBS_Z6_001:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34004_XS |  |  | JBS_Z6_001:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34013_XS |  |  | JBS_Z6_001:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34024_XS |  |  | JBS_Z6_031:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34027_XS |  |  | JBS_Z6_001:5:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34030_XS |  |  | JBS_Z6_021:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_34307_XS |  |  | JBS_Z6_001:5:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35001_XS |  |  | JBS_Z6_001:6:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35003_XS |  |  | JBS_Z6_031:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35004_XS |  |  | JBS_Z6_001:6:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35008_XS |  |  | JBS_Z6_031:5:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35035_XS |  |  | JBS_Z6_001:7:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_35047_XS |  |  | JBS_Z6_021:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39008_XS |  |  | JBS_Z6_041:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39031_XS |  |  | JBS_Z6_031:5:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39033_XS |  |  | JBS_Z6_021:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39157_XS |  |  | JBS_Z6_031:6:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39207_XS |  |  | JBS_Z6_021:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39358_XS |  |  | JBS_Z6_041:5:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39427_XS |  |  | JBS_Z6_041:5:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39435_XS |  |  | JBS_Z6_041:8:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39442_XS1 |  |  | JBS_Z6_041:6:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39442_XS2 |  |  | JBS_Z6_041:6:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39443_XS1 |  |  | JBS_Z6_041:7:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39443_XS2 |  |  | JBS_Z6_041:7:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39727_XS |  |  | JBS_Z6_041:8:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39742_XS1 |  |  | JBS_Z6_041:9:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39742_XS2 |  |  | JBS_Z6_041:9:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39743_XS1 |  |  | JBS_Z6_041:10:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_39743_XS2 |  |  | JBS_Z6_041:10:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_40030_XS |  |  | JBS_Z4_021:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_40201_XS |  |  | JBS_Z6_001:7:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_40308_XS |  |  | JBS_Z4_021:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_41020_XS |  |  | JBS_Z4_021:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_41201_XS |  |  | JBS_Z6_001:8:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_42027_XS |  |  | JBS_Z4_021:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_42201_XS |  |  | JBS_Z6_001:8:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_47505_XS |  |  | JBS_Z6_001:9:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_80012_XS |  |  | JBS_Z2_001:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_80018_XS |  |  | JBS_Z2_001:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82001_XS |  |  | JBS_Z2_021:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82013_XS |  |  | JBS_Z2_021:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82015_XS |  |  | JBS_Z2_002:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82042_XS1 |  |  | JBS_Z2_002:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82042_XS2 |  |  | JBS_Z2_002:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82043_XS1 |  |  | JBS_Z2_002:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_82043_XS2 |  |  | JBS_Z2_002:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83001_XS |  |  | JBS_Z2_021:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83013_XS |  |  | JBS_Z2_002:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83016_XS |  |  | JBS_Z2_021:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83042_XS1 |  |  | JBS_Z2_002:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83042_XS2 |  |  | JBS_Z2_002:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83043_XS1 |  |  | JBS_Z2_002:5:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_83043_XS2 |  |  | JBS_Z2_002:5:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84002_XS |  |  | JBS_Z2_002:6:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84013_XS |  |  | JBS_Z2_021:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84016_XS |  |  | JBS_Z2_021:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84042_XS1 |  |  | JBS_Z2_002:6:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84042_XS2 |  |  | JBS_Z2_002:7:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84043_XS1 |  |  | JBS_Z2_002:7:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_84043_XS2 |  |  | JBS_Z2_002:8:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85013_XS |  |  | JBS_Z2_021:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85016_XS |  |  | JBS_Z2_021:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85017_XS |  |  | JBS_Z2_002:8:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85042_XS1 |  |  | JBS_Z2_002:9:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85042_XS2 |  |  | JBS_Z2_002:9:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85043_XS1 |  |  | JBS_Z2_002:10:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_85043_XS2 |  |  | JBS_Z2_002:10:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_86009_XS |  |  | JBS_Z5_001:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_86013_XS |  |  | JBS_Z5_001:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_86016_XS |  |  | JBS_Z5_001:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_86201_XS |  |  | JBS_Z5_001:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_87003_XS |  |  | JBS_Z5_001:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_87012_XS |  |  | JBS_Z5_001:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_87014_XS |  |  | JBS_Z5_001:4:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_87201_XS |  |  | JBS_Z5_001:4:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_88012_XS |  |  | JBS_Z5_001:5:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_88014_XS |  |  | JBS_Z5_001:5:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_88015_XS |  |  | JBS_Z5_001:6:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_88201_XS |  |  | JBS_Z5_001:6:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_89554_XS |  |  | JBS_Z6_041:11:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_90001_XS |  |  | JBS_Z7_001:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_91001_XS |  |  | JBS_Z7_001:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_91201_XS |  |  | JBS_Z7_001:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_91501_XS |  |  | JBS_Z7_001:2:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_91506_XS |  |  | JBS_Z7_001:3:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_91601_XS |  |  | JBS_Z7_001:3:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_96201_XS |  |  | JBS_Z1_001:1:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_96202_XS |  |  | JBS_Z1_001:1:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_96209_XS |  |  | JBS_Z1_001:2:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_99002_XS |  |  | JBS_Z6_001:9:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_99004_XS |  |  | JBS_Z6_001:10:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_99302_XS |  |  | JBS_Z6_001:10:O.Pt02.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
ALIAS | Valves | O_XIS_99501_XS |  |  | JBS_Z6_001:11:O.Pt01.Data | (RADIX := Decimal, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_CoFeed_V3:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | Delivery_A |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | Delivery_B |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V3:AOI | TankInletValveInService | Dest Tank$NInlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_CoFeed_V3:AOI | HDR1InService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_CoFeed_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | onIncrementCnt |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | onsMaxTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | PrePromptAck |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | PostPromptAck |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | HDR1Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | HDR1Confirmed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locTankNumber |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locChaseEnabled |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locChaseSource |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locChaseReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locTankPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locDelivA_UL | Delivery A Upper Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locDelivA_LL | Delivery A Lower Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locDelivB_UL | Delivery B Upper Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | locDelivB_LL | Delivery B Lower Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V3:AOI | ZZZ_TestBit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_CoFeed_V4:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | Delivery_A |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | Delivery_B |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_CoFeed_V4:AOI | TankInletValveInService | Dest Tank$NInlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_CoFeed_V4:AOI | HDR1InService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_CoFeed_V4:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | onIncrementCnt |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | onsMaxTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | PrePromptAck |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | PostPromptAck |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | HDR1Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | HDR1Confirmed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locTankNumber |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locChaseEnabled |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locChaseSource |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locChaseReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locTankPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locDelivA_UL | Delivery A Upper Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locDelivA_LL | Delivery A Lower Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locDelivB_UL | Delivery B Upper Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | locDelivB_LL | Delivery B Lower Limit | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | ZZZ_TestBit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_CoFeed_V4:AOI | NoFlowRequired |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_DLY_MP4_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_MP4_V4:AOI | HDR1InService | Header 1 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | HDR2InService | Header 2 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | HDR3InService | Header 3 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | HDR4InService | Header 4 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | LoadCellDelivery | Source Tank $NLoad Cell$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | MeterDelivery | Meter$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | PumpInService | Source Tank$NPump$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | SourceOutletValveInService | Source Outlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | TankInletValveInService | Dest Tank$NInlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_MP4_V4:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | SourceTankInst |  | SM_SourceTankValidate_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | SM_ChaseWater |  | SM_ChaseWaterValve |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | Lock_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | SlugDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | Slug_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | MassFlowRateCutoff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | keepcapturingweight |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | MeterFlowRateCutoff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | tmrDestPRSfault |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | tmrDestPRSWarn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | FlowSPModeInitializeONS1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | FlowSPModeInitializeONS2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | locHDR1_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | locHDR2_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | locHDR3_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_MP4_V4:AOI | locHDR4_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_DLY_PMPALL_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_DLY_PMPALL_V4:AOI | HDR1InService | Header 1 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR2InService | Header 2 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR3InService | Header 3 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR4InService | Header 4 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR5InService | Header 5 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR6InService | Header 6 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR7InService | Header 7 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | HDR8InService | Header 8 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | SourceOutletValveInService | Source Outlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | MeterDelivery | Meter$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | LoadCellDelivery | Source Tank $NLoad Cell$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | PumpInService | Source Tank$NPump$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | TankInletValveInService | Dest Tank$NInlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_DLY_PMPALL_V4:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | SourceTankInst |  | SM_SourceTankValidate_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | SM_ChaseWater |  | SM_ChaseWaterValve |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | Lock_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | SlugDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | Slug_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | tmrDestPRSfault |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | tmrDestPRSWarn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | FlowSPModeInitializeONS1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | FlowSPModeInitializeONS2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR1_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR2_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR3_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR4_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR5_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR6_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR7_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_DLY_PMPALL_V4:AOI | locHDR8_ChangePathONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_INERT_V1:AOI | UDT |  | uEM_INERT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_INERT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_INERT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_INERT_V1:AOI | ValvesInService | Valves for Feed of Inert Gas | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_INERT_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_INERT_V1:AOI | SourceValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_INERT_V1:AOI | BypassValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_INERT_V1:AOI | BlanketValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_INERT_V1:AOI | VesselPrsInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_INERT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | PathConfirmed | Inlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_INERT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_PRS_Extension_Blanket_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
COMMENT | AA_PRS_Extension_Blanket_V1:AOI | UDT | Vacuum/Pressure Control Equipment Module Mode (0 = Seal, 1= Atm, 2= Scrub, 3=PRSCook, 4=Bleed, 5= Vac Pump) |  | UDT.SET.MODE
TAG | AA_PRS_Extension_Blanket_V1:AOI | VentValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | BypassValve | Bypass Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR1 | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR1Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR2Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR3Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR2PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR3PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR1Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR2Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | HDR3Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | onsHDR2ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | onsHDR3ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_Extension_Blanket_V1:AOI | PathOKVerTMR | Path OK Verification Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_PRS_RCH_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VentValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacPumpInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | PressureVentHDR | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacHDR | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | CoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | CoolWaterOutletTemp | Primary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacPumpInletPrs |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | LocalStartPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | LocalStopPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | VacBypassValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VentValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VacPumpInletValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VacPumpInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | PressureVentHDRInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VacHDRInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | CoolWaterFlowInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | CoolWaterOutletTempInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VesselPrsInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | VacPumpInletPrsInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | LocalStartPBInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | LocalStopPBInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | WaterInletValve | Seal Motor Water Inlet Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_RCH_V1:AOI | WaterInletValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_PRS_RCH_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR1Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR2Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR3Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR2PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR3PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR1Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR2Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | HDR3Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | onsHDR2ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | onsHDR3ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | PathOKVerTMR | Path OK Verification Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locVentValveCMDClose |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locVacPumpInletValveCMDClose |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locVacPumpInletValveCMDOpen |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_RCH_V1:AOI | locVentValveCMDOpen |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_PRS_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimVacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecVacBypassValve | Secondary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimVacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecVacPump | Secondary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | ScrubPumpRng | Scrubber Pump Running Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | HDR1 | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | HDR2 | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | HDR3 | Secondary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimCoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimCoolWaterInletTemp | Primary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimDemisterLS | Primary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecCoolWaterFlow | Secondary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecCoolWaterInletTemp | Secondary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecDemisterLS | Secondary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimHOA_InAuto_FS | Primary HOA Switch In Auto$N1=Auto | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | PrimHOA_InHand_FS | Primary HOA Switch In Auto$N1=Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecHOA_InAuto_FS | Secondary HOA Switch In Auto$N1=Auto | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | SecHOA_InHand_FS | Secondary HOA Switch In Auto$N1=Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_PRS_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | Open_FS | Open Field Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_PRS_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR1Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR2Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR3Release |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR2PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR3PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR1Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR2Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | HDR3Ready |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | onsHDR2ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | onsHDR3ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | PathOKVerTMR | Path OK Verification Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locScrubPumpInService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locVacPumpPrimInService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locHDR3InService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locHDR2InService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locHDR1InService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_PRS_V1:AOI | locVacPumpSecInService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_RECIRC_AOD_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1InService | Header 1 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2InService | Header 2 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3InService | Header 3 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | PumpInService | Source Tank$NPump$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | SourceOutletValveInService | Source Outlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | TankInletValveInService | Dest Tank$NInlet Valve$NIn Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_RECIRC_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1Confirmed | HDR1 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2Confirmed | HDR2 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3Confirmed | HDR3 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | OutletValveConfirmed | Outlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | InletValveConfirmed | Inlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | PumpConfirmed | Pump is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2PrevState | Header 2$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2Ready | Header 2$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3PrevState | Header 3$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3Ready | Header 3 $NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1PrevState | Header 1$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1Ready | Header 1$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR1PathMask |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR2PathMask |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDR3PathMask |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | tmrWaitForRMTimeout |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | onsHDR1ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | onsHDR2ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | onsHDR3ChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | UserInQueue |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | onsContinuousRecirc |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_RECIRC_AOD_V3:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_TEMPJK_V1:AOI | UDT |  | uEM_TEMPJK_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | HeatingInlet | Steam Supply$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | CoolingPump | Water Supply Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | HDR |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | BackupRTD | Backup RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPJK_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPJK_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | AA_TEMPJK_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | onsHDrChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | HDR1Ready | Header$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Malfunction_Warning_TON |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | State1310_Bool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | Safety_Reversion_Bit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | locSteamValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPJK_V1:AOI | locCoolingPumpInService |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_TEMPVC_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | BackupRTD | Backup RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | HDR1Ready | Header$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | onsHDrChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V1:AOI | onsHDrChangePath1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_TEMPVC_V2:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | PrimaryRTD | Primary RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | BackupRTD | Backup RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_V2:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | HDR1Ready | Header$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | onsHDrChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_V2:AOI | onsHDrChangePath1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_TEMPVC_VFD_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | Pump | Inlet Pump | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | BackupRTD | Backup RTD $NTemperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | AA_TEMPVC_VFD_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | HDR1PrevState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | HDR1Ready | Header$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | onsHDrChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_TEMPVC_VFD_V1:AOI | onsHDrChangePath1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | AA_VENT_V1:AOI | UDT |  | uEM_VENT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_VENT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_VENT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_VENT_V1:AOI | ValvesInService | Valves for Feed of Inert Gas | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | AA_VENT_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | AA_VENT_V1:AOI | SourceValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_VENT_V1:AOI | BypassValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_VENT_V1:AOI | ScrubValveInService |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | AA_VENT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | PathConfirmed | Inlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | AA_VENT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_AIN_V3:AOI | UDT |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | IN_Raw | Input Health for Associated Analog Card | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | IN_CHStatus | Input Channel Status | SINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | IN_InputHealth | Input Health for Associated Analog Card | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AIN_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AIN_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AIN_V3:AOI | STS_AlarmsEnabled |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AIN_V3:AOI | STS_SIM | Simulation Mode Is Active | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AIN_V3:AOI | IN_SuppressLevelAlarms |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_AIN_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AIN_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AIN_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AIN_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AIN_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_AIN_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_AOD_V3:AOI | UDT |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOD_V3:AOI | OUT_Run | Pump Solenoid | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_AOD_V3:AOI | IN_OutputHealth | Digital Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOD_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOD_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_AOD_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_AOUT_V3:AOI | UDT |  | uCM_AOUT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOUT_V3:AOI | OUT_CV | Signal to Field | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_AOUT_V3:AOI | IN_OutputHealth | Input Health for Associated Analog Card | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_AOUT_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOUT_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_AOUT_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_AOUT_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_DIFF_V3:AOI | UDT |  | uCM_DIFF_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DIFF_V3:AOI | HighReferenceDevice | High Reference Device | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DIFF_V3:AOI | LowReferenceDevice | Low Reference Device | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DIFF_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DIFF_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DIFF_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DIFF_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DIFF_V3:AOI | STS_AlarmsEnabled |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DIFF_V3:AOI | STS_SIM | Simulation Mode Is Active | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DIFF_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DIFF_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DIFF_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DIFF_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DIFF_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DIFF_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_DI_V5:AOI | UDT |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DI_V5:AOI | IN_Digital_Input | Digital In$NRaw Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DI_V5:AOI | IN_InputHealth | Digital In$NRaw Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DI_V5:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DI_V5:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DI_V5:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DI_V5:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DI_V5:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DI_V5:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | tmrFeedback | Max Allowable Feedback Time | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | tmrSIMDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DI_V5:AOI | onsReleaseSIM |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_DOUT_V3:AOI | UDT |  | uCM_DOUT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DOUT_V3:AOI | OUT_Output |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_DOUT_V3:AOI | InHealth_Output |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_DOUT_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DOUT_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_Enabled |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_Interlock |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_LocalInterlock |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | STS_SIM |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DOUT_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DOUT_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_DPHPAIR_V3:AOI | UDT |  | uCM_DPH_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_Cycle_CountA | Cycle Sensor Counts | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_Cycle_CountB | Cycle Sensor Counts | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | OUT_RunA | Run Output A | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | OUT_RunB | Run Output B | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_InputHealth_CycleA | Cycle Counter Input Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_InputHealth_CycleB | Cycle Counter Input Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_OutputHealthA | Output Channel Health Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | IN_OutputHealthB | Output Channel Health Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_Mode | Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_Run | Running Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_Faulted | Faulted Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_DPHPAIR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | PrimaryCPM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | tmrPairStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | tmrPairStopDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | FastestPumpCPM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | SecondaryCPM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_DPHPAIR_V3:AOI | SlowestPumpCPM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_E3001S_V3:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | IN_Status | Status Registers | AB:E300:I:3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | OUT_Control | Control Registers | AB:E300:O:1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | IN_Auto | HOA In Auto | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | IN_Hand | HOA In Hand | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | IN_Start | HOA In Start PB | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | IN_Stop | HOA In Stop PB | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | InHealth_Auto | HOA Input Health Auto | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | InHealth_Hand | HOA Input Health Hand | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | InHealth_Start | Input Health HOA In Start PB | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | InHealth_Stop | Input Health HOA In Stop PB | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_E3001S_V3:AOI | CM_M2S |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_E3001S_V3:AOI | loc_Agit_Man |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_E3001S_V3:AOI | onsLocalCFG |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_E3001S_V3:AOI | tmrTripReset | Maintain Trip Reset Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_HI4050_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | IN_Status |  | _0102:Hardy4000Series_D71801D4:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | OUT_Control |  | _0102:Hardy4000Series_0DB04C67:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | InHealth_Comm |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI4050_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_HI4050_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI4050_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_HI6500_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI6500_V3:AOI | IN_Status |  | _0102:Hardy6500Series_19FEEB66:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI6500_V3:AOI | OUT_Control |  | _0102:Hardy6500Series_74A2D67F:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI6500_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI6500_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_HI6500_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_HI6500_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | MeasurementUpdateCount |  | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | MeasurementUpdateMask |  | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | DataUpdating |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | tmrStaleData |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | onsStaleData |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_HI6500_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_IND560E_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | IN_Status |  | ME:IND560Enet_FLOAT_1Slots:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | OUT_Control |  | ME:IND560Enet_FLOAT_1Slots:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | InHealth_Comm |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND560E_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_IND560E_V3:AOI | In_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_IND560E_V3:AOI | In_DLYType |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_IND560E_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CmdAck | Current Value of Command Acknowledge | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CmdAckPrev | Previous Value of Command Acknowledge | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CommandAcked | Command Acknlowledged | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Command | Current Command | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CommandPrev | Previous Command | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Tare | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Clear | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | Zero | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | ProgrammableTare | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | CommandData | Commanded Tare Value | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | DataReturned | Data Type Returned From IND570 | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND560E_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_IND570E_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | IN_Status |  | ME:IND570Enet_FLOAT_1Slots:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | OUT_Control |  | ME:IND570Enet_FLOAT_1Slots:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | InHealth_Comm |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_IND570E_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_IND570E_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CmdAck | Current Value of Command Acknowledge | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CmdAckPrev | Previous Value of Command Acknowledge | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CommandAcked | Command Acknlowledged | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Command | Current Command | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CommandPrev | Previous Command | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Tare | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Clear | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | Zero | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | ProgrammableTare | Place Holder For Future Functionality | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | CommandData | Commanded Tare Value | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | DataReturned | Data Type Returned From IND570 | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_IND570E_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_2:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | IN_Running | Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | OUT_Run | Run Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | InHealth_Running | Input Health Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | OutHealth_Run | Output Health of Run | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2:AOI | CM_M2S |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_2:AOI | loc_Agit_Man |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_2_NoControl:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | IN_IsHI | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | IN_IsLO | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | OUT_HI | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | OUT_LO | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | LowToHiDelay |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | InHealth_IsHI | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | InHealth_IsLO | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | OutHealth_HI | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | OutHealth_LO | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_NoControl:AOI | CM_M2S_V2 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_2_NoControl:AOI | tmrLowToHiDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_2_OL:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | IN_Running | Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | IN_Overload | Overload Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | OUT_Run | Run Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | InHealth_Running | Input Health Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | InHealth_Overload | Overload Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | OutHealth_Run | Output Health of Run | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_2_OL:AOI | CM_M2S |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_2_OL:AOI | loc_Agit_Man |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_3:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | IN_Auto | Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | IN_Running | Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | OUT_Run | Run Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | InHealth_Auto | Input Health Auto | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | InHealth_Running | Input Health Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | OutHealth_Run | Output Health of Run | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_3:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_3:AOI | CM_M2S |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_3:AOI | loc_Agit_Man |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_4:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | IN_IsHI | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | IN_IsLO | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | OUT_HI | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | OUT_LO | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | InHealth_IsHI | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | InHealth_IsLO | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | OutHealth_HI | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | OutHealth_LO | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4:AOI | CM_M2S_V2 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_4_MOR:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | IN_IsHI | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | IN_IsLO | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | OUT_HI | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | OUT_LO | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | InHealth_IsHI | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | InHealth_IsLO | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | OutHealth_HI | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | OutHealth_LO | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_4_MOR:AOI | CM_M2S_V2 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_5:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | IN_AUTO | Auto Operation | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | IN_IsHI | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | IN_IsLO | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | OUT_HI | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | OUT_LO | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | InHealth_AUTO | Input Health Request Auto | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | InHealth_IsHI | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | InHealth_IsLO | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | OutHealth_HI | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | OutHealth_LO | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_5:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_5:AOI | CM_M2S_V2 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_GS_5:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | IN_Auto | Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | IN_Hand | Hand Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | IN_IsRunning | Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | IN_Disconnect | Disconnect | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | OUT_Run | Run Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | InHealth_Auto | Input Health Auto | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | InHealth_Hand | Hand Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | InHealth_Running | Input Health Is Running | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | InHealth_Disconnect | Disconnect Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | OutHealth_Run | Output Health of Run | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_GS_5:AOI | CM_M2S |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_GS_5:AOI | loc_Agit_Man |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_RCH_6:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | IN_Running | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | IN_Hand | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | OUT_Stop | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | OUT_Start | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | InHealth_Running | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | InHealth_Hand | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | OutHealth_Stop | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | OutHealth_Start | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_6:AOI | CM_M2S_V3 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Stop_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Stop_OSF_Output |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Stop_Flag |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Stop_Debounce_Timer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | CFG_NCStop |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Intermediate_Stop_Flag |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | OUT_Start_ID | Intermediate Start Flag in 3-wire assembly for M2S_RCH_6 | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Start_Debounce_Timer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Start_Flag | Start Flag in 3-wire assembly for M2S_RCH_6 | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_6:AOI | Start_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_RCH_7:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | IN_IsFastOrRev | Request High Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | IN_IsSlowOrFwd | Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OUT_FastOrRev | Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OUT_SlowOrFwd | Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OUT_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | InHealth_IsSlowOrFwd | Input Health Request Low Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | InHealth_IsFastOrRev | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OutHealth_SlowOrFwd | Output Health Run At HI Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OutHealth_FastOrRev | Output Health Run At LO Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | OutHealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_Enabled | AOI Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_RCH_7:AOI | CM_M2S_V2 |  | CM_M2S_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_7:AOI | Stop_Flag |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_7:AOI | Stop_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_RCH_7:AOI | Stop_Debounce_Timer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_M2S_V3:AOI | UDT |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_HOA_Hand | HOA - Hand Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_HOA_OFF | HOA - Off Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_HOA_Auto | HOA - Auto Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_ReqSlowOrFwd | Request Slow Speed Or Forward | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_ReqFastOrRev | Request Fast Speed Or Reverse | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_ReqSTOP | Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_IsSlowOrFwd | Running At Slow Speed Or Forward | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_IsFastOrRev | Running At$N Fast Speed Or Reverse | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_Disconnect | Disconnect Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | IN_Overload | Overload Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | OUT_SlowOrFwd | Run At Slow Speed Or Forward | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | OUT_FastOrRev | Run At Fast Speed Or Reverse | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_HOA_Hand | Input Health Manual Mode Request Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_HOA_OFF | Input Health Auto Mode Request Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_HOA_Auto | Input Health Auto Mode Request Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_ReqSlowOrFwd | Input Health Request Slow Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_ReqFastOrRev | Input Health Request Fast Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_ReqSTOP | Input Health Request Stop Push-Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_IsSlowOrFwd | Input Health Running At Slow Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_IsFastOrRev | Input Health Running At Fast Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_Disconnect | Input Health Disconnect Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InHealth_Overload | Input Health Overload Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | OutHealth_SlowOrFwd | Output Health Run At Slow Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | OutHealth_FastOrRev | Output Health Run At Fast Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_M2S_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_M2S_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | tmrMaxRunTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | HandStopONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_M2S_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_METDG_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_MassFlow |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_MassTotal |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_VolTotal |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_Density |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_DriveGain |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_Temp | Temperature Read From The Meter | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_CommStatus | Communication Status Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | IN_MeterFault | Meter Fault Status Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | InHealth_MeterFault | Meter Fault Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | MSG_Alarms | Faults Message to Meter | MESSAGE |  | (Usage := InOut, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METDG_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METDG_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | ReqUse |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | CM_MET |  | CM_MET_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | tmrFaultReadDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METDG_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_METP4_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | IN_RawFreq | Pulse Input for Counter Card Low 16 bit Word (Only Required in Counter Mode) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | IN_Density | The Density of the Current Raw Material | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | IN_InputHealth | Input Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | InHealth_Fault | Fault Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METP4_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METP4_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | ReqUse |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | CM_MET |  | CM_MET_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsVolume |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsMass |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsCheck |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | localMassTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | localVolumeTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | localPrevMassTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsRollOver |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | localPrevVolumeTotal |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsRollOverVol |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | onsRollOverMass |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METP4_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_METPAIR_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | Meter1 |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | Meter2 |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | ActiveMeter | Currently Active Meter | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | MeterForComplete | Meter Monitored For Complete Status$N | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPAIR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locMassTotal1 |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locVolumeTotal1 |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locVolumeTotal2 |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locMassTotal2 |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locComplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | onsMeter1Zero |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | onsMeter2Zero |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locPrevAutoEnable1 |  | DINT[17] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locPrevAutoEnable2 |  | DINT[17] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locInUse |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | InUseResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | InUseRef |  | DINT[17] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | InUseCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locPrevRunning |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | CurrentUserID |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | prevActiveMeter | ActiveMeter Value From Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locMeterTransition | Active Meter Is Transitioning | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | prevMeterForComplete | MeterForComplete Value From Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locMeter1Activated |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPAIR_V3:AOI | locMeter2Activated |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_METPG_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | IN_RawMass | Pulse Input for Counter Card Low 16 bit Word (Only Required in Counter Mode) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | IN_RawVolume | Pulse Input for Counter Card Volume Pulse | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | IN_MeterFault | Meter Fault Status Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | InHealth_RawMass | Input Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | InHealth_RawVolume | Input Volume Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | InHealth_MeterFault | Meter Fault Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_METPG_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_METPG_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | ReqUse |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | CM_MET |  | CM_MET_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | onsRollOverMass |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | onsRollOverVol |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | localPrevVolumeTotal |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | localPrevMassTotal |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_METPG_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_MET_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_MassFlow |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_MassTotal |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_VolFlow |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_VolTotal |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_Density |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_Temp | Temperature Read From The Meter | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_DriveGain |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | IN_CommStatus | Communication Status Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | InHealth_Inputs | Meter Fault Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MET_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MET_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | ExternalFault | External Fault Is Triggered | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | NotFaultedONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsTolerance | Tolerance Evaluation ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | ProdZoneFltReset | Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsZoneFltReset | Zone Fault Reset ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsProdZoneFltReset | ONS Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | bInUse | Being Used Or In Manual | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | bAutoCmdInMan | Auto Command In Manual Received | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsEnabled |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsInitMeterTotal_VOL | Initial Meter Total One-Shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsInitMeterTotal_Mass | Initial Meter Total One-Shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | onsAlarmsEnabled | Alarms Enabled One Shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrRunTime | Total Run Time Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrFlowRateTotal | Timer used to accumulate time since the last scan to Accumulate Total | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrMassFlowRateAcc | Timer used to accumulate time since the last scan | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrStable | Stablize Timer Delay time once the stop or complete is issued | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrSettle | Settle Timer Once a Start Command is Issued | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrLowFlow | Low Flow Timer | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | CM_MET_V3:AOI | InUseResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | InUseCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rTotalPreviousScan_VOL | Total Volume during the Scan | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rTotalSinceInit_VOL | Accumulated Total Volume Since the Last Initial Value was Captured | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rCapturedTotal_VOL | Captured Total Volume Since last Rollover | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rInitMeterTotal_VOL | Initial Meter Total Volume Captured on the Start of a Addition | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rTotalPreviousScan_Mass | Total Amount during the Scan | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rAccPulseTotal | Pulses Accumulated from Start as REAL | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rAccFlowTotal | Total Accumulated from Flow Rate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rFlowTotalPerScan | Total Accumulated from Flow Rate during this Scan | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rTotalSinceInit_Mass | Accumulated Total Since the Last Initial Value was Captured | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rCapturedTotal_Mass | Captured Total Since last Rollover | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | rInitMeterTotal_Mass | Initial Meter Total Captured on the Start of a Addition | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | InUseRef |  | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | PrevInUseBy1 | Previous In Use By Result 1 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | PrevInUseBy0 | Previous In Use By Result 0 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | FltActive | Status Of All Active Faults/Warnings | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | CMDAutoDINT | Number of DINTs Used In Auto Command | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | CMDAutoZeroSize | Size of The Auto Zero Registers | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | CMDAutoSizeMan | Offset Size Of The Auto Array When In Manual | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | FltLockOut | Fault Lock-Out Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | InUseBy1 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | InUseBy0 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | dintWrkgRunHrs | Working Amount of Run Time Hours | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | nMassFlowRatePreviousTime | Flow Rate Calculation Time at the last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | nMassFlowRateDeltaTime | Flow Rate Calculation Time Accumulated Since the Last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | AutoCMDMan |  | SM_AutoCMDMan_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrVolumeFlowRateAcc | Timer used to accumulate time since the last scan | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | nVolumeFlowRatePreviousTime | Flow Rate Calculation Time at the last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | nVolumeFlowRateDeltaTime | Flow Rate Calculation Time Accumulated Since the Last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrLowDensity | Low Density Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MET_V3:AOI | tmrHiDensity | Hi Density Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_MM5700IP_V3:AOI | UDT |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MM5700IP_V3:AOI | IN_Status | Input Data | _0392:002B_0048_0C3CE510:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MM5700IP_V3:AOI | OUT_Control | Output Data | _0392:002B_0048_E2E31DE3:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MM5700IP_V3:AOI | IN_StopTotals | Stop Totalizers | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MM5700IP_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_MM5700IP_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | ReqUse |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | CM_MET |  | CM_MET_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | tmrNotFullDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | tmrResetTotal |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | onsResetTotal |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | internalEN | Internal Enable bit | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_MM5700IP_V3:AOI | tmrExtremePrimaryPurposeVariableDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_PID_V3:AOI | UDT |  | uCM_PID_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | IN_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | IN_ProcessValue | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | OUT_ControlValue | Output Control Variable | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PID_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PID_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | RateSetpoint | Rate Setpoint$NTo Ramp Controller | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | PrevRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | PrevRampRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | CalRampRate | Calculated Ramp$NRate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | ActiveRampingSetpoint | Ramping Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | KPStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | KIStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | KDStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PID_V3:AOI | onsInControl |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_PMR_V3:AOI | UDT |  | uCM_PMR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | IN_PanelEstop | Panel Estop | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | IN_PumpFault | Pump Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | Output | AOI Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | DisableOutput | Disable Output From Pump | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | InHealth_PanelEstop | Input Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | InHealth_PumpFault | Input Channel Health Of Pump Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | InHealth_Output | Output Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | InHealth_DisableOutput | Output Channel Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_PMR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_Mode | CM Auto/Manual Mode$NAUTO = 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_InUse | CM Is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_Faulted | CM Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_Interlock | CM Interlock Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | STS_SIM | CM Simulation Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_PMR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PMR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PMR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PMR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_PMR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_PMR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_SF_V3:AOI | UDT |  | uCM_SF_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_SF_V3:AOI | IN_FaultInput | Raw Fault Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_SF_V3:AOI | IN_InputHealth | Input Health Of Fault Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_SF_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_SF_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_SF_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_SF_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_SF_V3:AOI | UsingArraySize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_SF_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_SZONE_V3:AOI | UDT |  | uCM_ZON_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | IN_Interlock | Zone Interlock Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | IN_RevInterlock | Zone Interlock Input Is Reverse Operation | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | IN_ResetPB | E-Stop Relay Reset Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | OUT_Reset | E-Stop Relay Reset Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | InHealth_Interlock | Zone Interlock Input Card Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | InHealth_ResetPB | E-Stop Relay Reset Push Button Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | OutHealth_Reset | E-Stop Relay Reset Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_SZONE_V3:AOI | ZoneID | Zone ID Number | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_SZONE_V3:AOI | STS_SIM | System Is In Simulation | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_SZONE_V3:AOI | STS_InterlockOK | Zone Interlock Is OK | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_SZONE_V3:AOI | STS_RevInterlock | System Is In Reverse Operation Mode | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_SZONE_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_SZONE_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V2WHR_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_ClosedLS1 | Limit Switch Closed Connection1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_OpenedLS1 | Limit Switch Open Connection1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | OUT_Out1 | Device Output 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_ClosedLS2 | Limit Switch Closed Connection2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | IN_OpenedLS2 | Limit Switch Open Connection2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | OUT_Out2 | Device Output 2 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_ClosedLS1 | Close Limit Switch Input Health 1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_OpenedLS1 | Open Limit Switch Input Health 1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | OutHealth_Out1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_ClosedLS2 | Close Limit Switch Input Health 2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InHealth_OpenedLS2 | Open Limit Switch Input Health 2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | OutHealth_Out2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WHR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | CM_V2WH_V3_AOI |  | CM_V2WH_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_OUT2Health |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_OUT1Health |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_IN_OPNHealth |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_IN_CLSHealth |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_OUT_Out2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_OUT_Out1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_IN_OpenedLS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | Mapped_IN_ClosedLS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | OperationFailTMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | OperationOK |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | OperationFailCTR |  | COUNTER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WHR_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V2WH_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | IN_ClosedLS | Limit Switch Closed Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | IN_OpenedLS | Limit Switch Open Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | IN_Auto | HOA Auto Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | IN_Hand | HOA Hand Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | InHealth_ClosedLS | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | InHealth_OpenedLS | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | InHealth_Auto | HOA Auto Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | InHealth_Hand | HOA Hand Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | OutHealth_Out1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | OutHealth_Out2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WH_V3:AOI | Is_XIHR |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_V2WH_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | CM_V2W_V3_AOI |  | CM_V2W_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | AutoHOAncONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | AutoHOAnoONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WH_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V2WR_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | IN_ClosedLS1 | Limit Switch Closed Connection1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | IN_OpenedLS1 | Limit Switch Open Connection1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | OUT_Out1 | Device Output 1 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | IN_ClosedLS2 | Limit Switch Closed Connection2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | IN_OpenedLS2 | Limit Switch Open Connection2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | OUT_Out2 | Device Output 2 | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | InHealth_ClosedLS1 | Close Limit Switch Input Health 1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | InHealth_OpenedLS1 | Open Limit Switch Input Health 1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | OutHealth_Out1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | InHealth_ClosedLS2 | Close Limit Switch Input Health 2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | InHealth_OpenedLS2 | Open Limit Switch Input Health 2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | OutHealth_Out2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2WR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | CM_V2W_V3_AOI |  | CM_V2W_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_OUT2Health |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_OUT1Health |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_IN_OPNHealth |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_IN_CLSHealth |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_OUT_Out2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_OUT_Out1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_IN_OpenedLS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | Mapped_IN_ClosedLS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | OperationFailTMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | OperationOK |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | OperationFailCTR |  | COUNTER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | ONSCustomFaults |  | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentLSMismatchTMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentPrevSolenoidUsed |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentSIM_ClosedLS1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentSIM_ClosedLS2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentSIM_OpenedLS1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentSIM_OpenedLS2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | RedundentCheckCustomFaultsTMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2WR_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V2W_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_ClosedLS | Limit Switch Closed Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_OpenedLS | Limit Switch Open Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_CLSHealth | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_OPNHealth | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_Out1Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | IN_Out2Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V2W_V3:AOI | Is_XIHR | Valve is AOI type with redundant hand control | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_V2W_V3:AOI | Is_XISR | Valve is AOI type with redundant control | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | CM_V2W_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | ExternalBit | External Fault Bit Including Offset | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | ExternalFault | External Fault Is Active | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | onsExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | EnableExternalFaultInSIM |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V2W_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V3D_V3:AOI | UDT |  | uCM_V3D_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_ToA_LS | Limit Switch Straight Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_ToB_LS | Limit Switch Divert Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_ToA_Health | Input Health To A LS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_ToB_Health | Input Health To B LS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_Out1Health | Output Health of Out1 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | IN_Out2Health | Output Health of Out2 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3D_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_In_Use | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_ToA | Diverted To A | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_ToB | Diverted To B | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_NormalToB | Normal To B Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3D_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3D_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_V3W_V3:AOI | UDT |  | uCM_V3W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_StraightLS | Limit Switch Straight Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_DivertLS | Limit Switch Divert Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_STRHealth |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_DIVHealth |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_Out1Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | IN_Out2Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Straight |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Divert |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_NormalDivert | Normal Divert Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_V3W_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_V3W_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VDB_V3:AOI | UDT |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | IN_ClosedLS | Limit Switch Closed Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | IN_OpenedLS | Limit Switch Open Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | IN_DribbleLS | Limit Switch Dribble Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OUT_Open | Open Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OUT_Dribble | Dribble Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Closed | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Open | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InHealth_Dribble | Dribble Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | OutHealth_Dribble | Dribble Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Dribble | Valve In Dribble Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VDB_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | locManDribble |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | onsToDribble |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | locDribbleFromOpen |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VDB_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD2S_MOR_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_Running |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_AtRef |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_LO |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_HI |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_Run |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InHealth_Running |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InHealth_AtRef |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_LO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_HI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD2S_MOR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD2S_MOR_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD525Ctrl_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_VFD |  | AB:PowerFlex525V_E_ABF89C61:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_VFD |  | AB:PowerFlex525V_EENET_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InHealth_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD525Ctrl_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD525Ctrl_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD755_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_VFD |  | AB:PowerFlex755_E_3F9B8FFE:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OUT_VFD |  | AB:PowerFlex755_EENET_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_LowSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_HighSpeedSetpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_ReqLO |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InHealth_ReqHI |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD755_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD755_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDANA_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | LevelIndicator |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OUT_Ref |  | INT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | InHealth_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | OutHealth_Scaled |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDANA_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ConditionedOut |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDANA_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDCH_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | IN_Status |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | OUT_Command |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | RunForward |  | OUT_Command.0
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | RunReverse |  | OUT_Command.1
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | Reset Drive Fault |  | OUT_Command.3
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | NetControl |  | OUT_Command.5
COMMENT | CM_VFDCH_V3:AOI | OUT_Command | NetReference |  | OUT_Command.6
TAG | CM_VFDCH_V3:AOI | OUT_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | CommStatus |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | InHealth_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | OutHealth_Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | DriveMSG | Drive Communication | MESSAGE |  | (Usage := InOut, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDCH_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | tmrMSGInterval | Data Via Message Interval Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | MsgState | Message State Engine | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CIPMessage | CIP Message Configs | SM_CIPMsg_V1[5] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CIPConfig | CIP Read Drive Configs | SM_CIPMsg_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CFGState | Config Message State | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | DINStatus | Digital In Status Of Drive | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
COMMENT | CM_VFDCH_V3:AOI | DINStatus | HOA In Auto |  | DINStatus.0
COMMENT | CM_VFDCH_V3:AOI | DINStatus | Drive Enabled |  | DINStatus.1
TAG | CM_VFDCH_V3:AOI | VFDFaultCode | VFD Fault Code - Read Only If Fault Exists | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ReqRunHold | Request Run Hold Register | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsMsgErr | Message Error ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | RawSpeedActual |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | DriveState | 1=Startup, 2=NotReady, 3=Ready, 4=Enabled, 5=Stopping, 6=FaultStop, 7=Faulted | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | RefCmd | Scale Commanded Reference | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | ParamMSGFailed | Drive Reference Parameter Error | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsProcessReadData |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsResult |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsReadConfig |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | onsHOA_OFF |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDCH_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF700_V1:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_VFD |  | AB:PowerFlex700VC_DE65F68A:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OUT_VFD |  | AB:PowerFlex700VC_C4120625:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V1:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF700_V2:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_VFD |  | AB:PowerFlex700VC_DE65F68A:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OUT_VFD |  | AB:PowerFlex700VC_C4120625:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF700_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF700_V2:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF70_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_VFD |  | AB:PowerFlex70_EB4AE803:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OUT_VFD |  | AB:PowerFlex70_A9D06D0C:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF70_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF70_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFDPF753_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_VFD |  | AB:PowerFlex753_R_3F9B8FFE:I:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OUT_VFD |  | AB:PowerFlex753_ENETR_Drive:O:0 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_LowSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_HighSpeedStpt |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OUT_Enable | Enable Output To Drive | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Start |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | Inhealth_Stop |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Hand |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Auto |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InHealth_Disconnect |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | OutHealth_Enable | Enable Output To Drive Health | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFDPF753_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CM_VFD |  | CM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | ReqUse | Monitor Requested Use | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFDPF753_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VFD_V3:AOI | UDT |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Start | Start Drive Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Stop | Stop Drive Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Disconnect | Disconnect Switch Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Running | Running Forward or Reverse | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_ReqREV | Request Reverse Operation | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Warning | Drive Warning | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Ready | Drive Ready | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_NetCtrl | Controlled From Network | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_NetRef | Reference From Network | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_AtRef | At Reference Speed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Accel | Accelerating | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_Decel | Decelerating | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | OUT_Ref |  | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | CommStatus |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | InHealth_Inputs | Start Drive Input Health Status | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | InHealth_Outputs | Manual Mode Request Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Faulted | Control Module Fault Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Mode | Auto Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_InUse | Module is In Use | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VFD_V3:AOI | OUT_Reference | Output Reference (0-100%) | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_VFD_V3:AOI | IN_FailToRunDelay |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_VFD_V3:AOI | AutoCMDMan | Auto Command In Manual Monitor | SM_AutoCMDMan_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | SpeedValidate | Speed Validation Holding Register | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrRunTime | Total Run Time Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrFailedToRun | Failed To Run Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrResetVFD | Reset Hold To VFD | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseRef |  | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseBy1 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | InUseBy0 | In Use By Register (Used for Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FltLockOut | Fault Lock Out Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | dintWrkgRunHrs | Working Amount of Run Time Hours | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | PrevInUseBy1 | Previous In Use By Result 1 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | PrevInUseBy0 | Previous In Use By Result 0 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | MsgParamVal | Returned Parameter From internal Message | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ModuleStatus | Fault/Warning Status (>0=Fault;<0=Warn) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FltActive | Status Of All Active Faults/Warnings | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CMDAutoDINT | Number of DINTs Used In Auto Command | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CMDAutoSizeMan | Offset Size Of The Auto Array When In Manual | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsMsgType | Message ONS | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | RefCmd | Commanded Reference | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | NotFaultedONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | bAutoCmdInMan | Auto Command In Manual Received | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | bInUse | Being Used Or In Manual | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsAutoRunRequest | Auto Run Request Is Issued ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsNotInUseSpeed | Not In Use ONS for Speed Ref | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsZoneFltReset | Zone Fault Reset ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsProdZoneFltReset | ONS Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ProdZoneFltReset | Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ExternalFault | External Fault Is Active | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | onsExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | ExternalBit | External Fault Bit Including Offset | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | RateSetpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KPStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KIStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | KDStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | tmrMaxRunTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VFD_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VPRANA_V3:AOI | UDT |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_CloseLS | Close Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | CM_VPRANA_V3:AOI | IN_OpenLS | Open Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | CM_VPRANA_V3:AOI | IN_AnalogLS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OUT_Solenoid | Energize Block Solenoid | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OUT_CV | Output Control Variable | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | IN_Status | Analog Channel Status | SINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | InHealth_CloseLS | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | InHealth_OpenLS | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | OutHealth_CV | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | SetLSClosed | Set Closed Limit Switch Value When Using Analog Feedback | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Open |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_NormalOpen | Normal Divert Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPRANA_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPRANA_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | RateSetpoint | Rate Setpoint$NTo Ramp Controller | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | PrevRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | PrevRampRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | CalRampRate | Calculated Ramp$NRate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | ActiveRampingSetpoint | Ramping Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KPStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KIStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | KDStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | locTaskRate |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPRANA_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VPR_V3:AOI | UDT |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_CloseLS | Close Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_OpenLS | Open Limit Switch Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_FlowRate | Flow Rate$NInput from $Nthe Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OUT_Solenoid | Energize Block Solenoid | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OUT_CV | Output Control Variable | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | IN_Status | Analog Channel Status | SINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | InHealth_CloseLS | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | InHealth_OpenLS | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OutHealth_Open | Open Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | OutHealth_CV | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | PIDLoop | PID Loop | PID |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_InUse |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Open |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_NormalOpen | Normal Divert Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_AnalogInput | HART Analog Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_Travel | HART Travel Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_SupplyPrs | HART Input Supply Pressure | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | IN_DriveSignal | HART Drive Signal | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VPR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | RateSetpoint | Rate Setpoint$NTo Ramp Controller | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PrevRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PrevRampRateSetpoint | Previous Ramp$NRate Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | CalRampRate | Calculated Ramp$NRate | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ActiveRampingSetpoint | Ramping Setpoint | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | Woundup_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KPStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KIStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | KDStorage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | locTaskRate |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrDriveSignalHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | DriveSignalHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | DriveSignalLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrDriveSignalLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrAnalogInputHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AnalogInputHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrAnalogInputLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | AnalogInputLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrSupplyPrsHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | SupplyPrsHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrSupplyPrsLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | SupplyPrsLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrTravelHiAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | TravelHiAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrTravelLoAlm |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | TravelLoAlmPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | tmrPositionFlt |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | PositionFltPre |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | ValvePosDiff | Valve Position Difference | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | HartVlvFlt |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VPR_V3:AOI | CM_Interlock |  | SM_Interlock_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_VSL_V3:AOI | UDT |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_CloseCMD | Close Command From Master | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OpenCMD | Open Command From Master | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_ModeCMD | Automatic Mode Command | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_ClosedLS | Limit Switch Closed Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OpenedLS | Limit Switch Open Connection | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | OUT_Out1 | Device Output 1$NUsed to Open a 2 Way Valve or change to Divert Postion on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | OUT_Out2 | Device Output 2 (Optional)$NUsed to Close a 2 Way Valve or change the Postion to straight on a 3 Way Valve | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_CLSHealth | Close Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_OPNHealth | Open Limit Switch Input Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_Out1Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | IN_Out2Health |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Mode |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_In_Use |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Closed |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Opened |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_NormalOpen | Normal Close Type Valve Configuration | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_VSL_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | LastUser |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locAutoInUse |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_VSL_V3:AOI | locInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WSGE_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | BaseResolution |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Invert |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit4 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit8 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit10 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit20 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit40 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit80 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit100 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit200 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit400 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit800 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit1000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit2000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit4000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit8000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit10000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit20000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit40000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Bit80000 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | Sign |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | InHealth | Control Variable Output Health | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSGE_V3:AOI | ScaleReal | Scale Value | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDIn | Input BCD as DINT | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDConditioned |  | DINT |  | (RADIX := Binary, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | uWeight | Unsigned Weight From BCD | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | RawWeight | Signed Weight | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | BCDValid |  | SM_BCDMonitor_V1[5] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | EnableCustom0 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSGE_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WSP_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | IN_RawWeight | Raw Weight$Nfrom the Weigh Scale | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | IN_DisableIntegrityFLT | Disable Data Integrity Alarms | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_WSP_V3:AOI | InHealth_Comm |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | ProdLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WSP_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | CM_WS |  | CM_WS_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | NotInUse | Object Is Not Currently Being Used | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ReqUse |  | SM_RequestUse_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseByAOI |  | SM_InUseByUsing_V3[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | OSFOutput |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | OSFStorage |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | CMDSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ScaleInts |  | INT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ScaleReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | SwapReg | Word Swap Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | ConfigDataRead |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | tmrDataON | Data Integrity Bit ON | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | tmrDataOFF | Data Integrity Bit OFF | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | IntOffset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WSP_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | CM_WS_V3:AOI | UDT |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | IN_RawWeight | Raw Weight$Nfrom the Weigh Scale | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | InHealth_RawWeight | Input Health of I/O Point | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | CM_WS_V3:AOI | STS_Enabled | CM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Mode | Mode Status (Auto=1;Man=0) | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_InUse | In Use Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Faulted | Module Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_Interlock | Safety Interlock Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_LocalInterlock | Localized Interlock Signal | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | STS_SIM | Simulation Mode Status | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | CM_WS_V3:AOI | IN_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | CM_WS_V3:AOI | IN_DLYType |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | CM_WS_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsInitCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsNotRunning | Not Running ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoLoss | Auto Loss ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoGain | Auto Gain ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsNumofCycles | Number of Cycles One Shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bAutoCmdInMan | Auto Command In Manual Received | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bInUseLoss | Being Used Or In Manual Loss | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | bInUseGain | Being Used Or In Manual Gain | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | CM_WS_V3:AOI | SimInit | Simulation Initialize Values | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsAutoStab | Auto Stabilize ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsSettle | Settling ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsProdZoneFltReset | ONS Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ProdZoneFltReset | Controlling EM/EP Has Issued a Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsZoneFltReset | Zone Fault Reset ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsInitMeterTotal |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | HI | High Limit Exceeded | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LO | Low Limit Exceeded | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | NotFaultedONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsTolerance | Tolerance Evaluation ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LossBy1 | Loss By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | LossBy0 | Loss By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | GainBy1 | Gain By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | GainBy0 | Gain By (Used For Indirect Address) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | PrevInUseBy1 | Previous In Use By Result 1 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | PrevInUseBy0 | Previous In Use By Result 0 | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | nFlowRatePreviousTime | Flow Rate Calculation Time at the last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | nFlowRateDeltaTime | Flow Rate Calculation Time Accumulated Since the Last Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FltActive | Status Of All Active Faults/Warnings | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FaultCodeHolding | Fault Code Holding Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoDINT | Number of DINTs Used In Auto Command | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoZeroSize | Size of The Auto Zero Registers | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CMDAutoSizeMan | Offset Size Of The Auto Array When In Manual | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | SimWeight | Simulation Weight Value (Used in Sim Mode Only) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rFlowRatePeriodWeight |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rWeightPerScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rCapturedTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rTotalSinceInit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rInitMeterTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rTotalPreviousScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | StoredWeight |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoRef |  | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCMD | OR Values For AutoOpen and AutoClose | DINT[39] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FltLockOut | Fault Lock Out Register | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrSim |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | StableTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrLowFlow | Low Flow Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrFlowRateAcc | Timer used to calculate the flow rate | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrLoFaultDelay | LO Fault Delay Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | tmrHiFaultDelay | HI Fault Delay Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoResltCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCmpCntrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoCMDMan |  | SM_AutoCMDMan_V1[2] |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExternalFault | External Fault Is Triggered | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | AutoEnableInst |  | SM_CMDAutoOR_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateCTL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateCTL2 |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateAve_Unload |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | FlowRateArray |  | REAL[20] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | flowenable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | onsflowenable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | CM_WS_V3:AOI | rWeightPerScanTest |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | ConvertToElapsedTime:AOI | Input_Timer |  | TIMER |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | ConvertToElapsedTime:AOI | Output_ElapsedTime |  | TIME_ELAPSED |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | ConvertToElapsedTime:AOI | CountDown |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | ConvertToElapsedTime:AOI | Secs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Hrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Mins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | RemainingSecsFromHrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | RemainingSecsFromMins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Secs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Hrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_RemSecsFromHrs |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Mins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_RemSecsFromMins |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | Setpoint_Mins_Reduced |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | SET_MIN_Scaled |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | SET_SECS_Scaled |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | TimeValueMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | AccumMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | ConvertToElapsedTime:AOI | PresetMS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_ADDPOT_V1:AOI | UDT |  | uEM_ADDPOT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | TopInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | BotInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_ADDPOT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_ADDPOT_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_AGIT_M2S_V3:AOI | UDT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | Motor |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | MixTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCycleAgitationOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrCycleAgitationOn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevInLowSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | PrevInHighSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Agitator_Reference_Val |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ModeChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Inst_ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedMixTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedCycleOffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedCycleOnTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrMaxAgitTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | onsMaxAgitTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | onsMaxAgitFLT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAgitHeldInCycle |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_M2S_V3:AOI | tmrMaxAgitTimeInAgitation |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_AGIT_VFD_V3:AOI | UDT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | Motor |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_AGIT_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | MixTimer |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCycleAgitationOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrCycleAgitationOn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevInLowSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | PrevInHighSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Agitator_Reference_Val |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ModeChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedMixTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedCycleOffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedCycleOnTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ElapsedMixTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrMaxAgitTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | onsMaxAgitTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | ShutoffTimeRemaining |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | onsMaxAgitFLT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAgitHeldInCycle |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_AGIT_VFD_V3:AOI | tmrMaxAgitTimeInAgitation |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CoFeed_V2W_V2W_V3:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryA |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryA_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryB |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | DeliveryB_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | Cofeed_AOI |  | AA_CoFeed_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CoFeed_V2W_V2W_V3:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CoFeed_V2W_V2W_V4:AOI | UDT |  | uEM_CoFeed_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryA |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryA_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryB |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | DeliveryB_Valve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | Cofeed_AOI |  | AA_CoFeed_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CoFeed_V2W_V2W_V4:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_CONT_DLY_V1:AOI | UDT |  | uEM_CONT_DLY_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | Scale |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_CONT_DLY_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ContIndex | Used to Search For Matching Container | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RMIndex | Raw Material Index Used For Finding Raw Material in a Container | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_Cont |  | udsContTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTContIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Blank_RM |  | udsMatTracking[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ScaleIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_Tare |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ReweighActive |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | ContAmt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Container_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Container_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RM_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | RM_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Cont_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | Cont_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTCont_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_CONT_DLY_V1:AOI | UDTCont_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RW_Source | Rework Source Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Water_Source |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Source | Washwater Delivery Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | NonGPWW_Source | Non Generic Paint Washwater Source | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | MaxGPToAllowWater | Maximum GP Percentage before$Nswitching to Virgin Water is NOT allowed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | EnableWWFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Delivery_Done |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Delivery_Active |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | WW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | RW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SetpointRef |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | SetpointChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DGP_V2W_AOD_R_V4:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RW_Source | Rework Source Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Water_Source |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Source | Washwater Delivery Constant | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | NonGPWW_Source | Non Generic Paint Washwater Source | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | MaxGPToAllowWater | Maximum GP Percentage before$Nswitching to Virgin Water is NOT allowed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | EnableWWFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Delivery_Done |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Delivery_Active |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | WW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | RW_Initial_Flush_Complete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SetpointRef |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DGP_V2W_AOD_R_V4:AOI | SetpointChanged |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_PREWEIGH_V1:AOI | UDT |  | uEM_DLY_PREWEIGH_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | sContainer |  | udsContTracking[50] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_Status |  | uEM_STATUS_V1[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | stsIndex |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_DLY_PREWEIGH_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_PREWEIGH_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_STATUS_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_STATUS_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_PREWEIGH_V1:AOI | MatchLotNumb |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_SCALE_V1:AOI | UDT |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | valContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Scale_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | Scale_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DLY_EarlyComplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ActiveFinal_Test |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | DeliveryDiff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V1:AOI | ActualLastScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_SCALE_V2:AOI | UDT |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | SCALE |  | uCM_WS_V3[20] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | EM_Status |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | Barcode |  | udsBarcodeStrings |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_SCALE_V2:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | RMIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | lclString |  | STRING[10] |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Blank_RM |  | udsMatTracking |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | lclContIndex | Local Container Index For Multiple Containers being Used in Preweigh | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ScaleIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Tare | String Representing Tare | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Start |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLYIndex |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | strEM_DLY_SourceTank |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_GetWeight |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | valContIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_NextCont |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | String_Complete |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_SCALE_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | EM_SCALE_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Scale_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | Scale_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DLY_EarlyComplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ActiveFinal_Test |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | DeliveryDiff |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_SCALE_V2:AOI | ActualLastScan |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_CHASE_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | PurgeValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_PURGE_V3:AOI | tmrAirPurge |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourcePump |  | uCM_DPH_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_DPH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourcePump |  | uCM_DPH_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_DPH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_DPH_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_PMR_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourcePump |  | uCM_PMR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_PMR_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | tmrMeterPumpIn |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_PMR_V3:AOI | MeterPumpInACC |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_PMPALL_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V2W_VFD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V2W_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V2W_VFD_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V3W_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | TankInletValve |  | uCM_V3W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_V3W_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | TankInletValve |  | uCM_V3W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_V3W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_V3W_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VDB_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | TankInletValve |  | uCM_VDB_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VDB_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VDB_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceOutletValve1 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceOutletValve2 |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | WaterValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | InitialAmountToStartPump |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | PumpDelayOffSec |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrPumpDelayOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | STS_FillingTube |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_SADD_V3:AOI | tmrFillingTube |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_AOD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_AOD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR7 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HDR8 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | UDT_DLY |  | AA_DLY_PMPALL_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_PMPALL_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_R_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Recirc |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_R_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_DLY_VPR_VFD_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | TankInletValve |  | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | DestPRS |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_DLY_VPR_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_DLY_VPR_VFD_V3:AOI | onsDribbleSpeed |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_HOLD_V1:AOI | UDT |  | uEM_HOLD_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_HOLD_V1:AOI | ExternalReset | External Timer Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | ExternalHold | External Timer Hold | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_HOLD_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | HoldTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_HOLD_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_INERT_V2W_V1:AOI | UDT |  | uEM_INERT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | SourceValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | BlanketValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | BypassValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | InertFlowRate | Inert Gas Flow Rate | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | VesselPrs |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_INERT_V2W_V1:AOI | UDT_DLY |  | AA_INERT_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | Deadband_Cooling |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | Deadband_Heating |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | HighDeadband |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | LowDeadband |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_INERT_V2W_V1:AOI | PrsDebounce |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PMPT_V1:AOI | UDT |  | uEM_PMPT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PMPT_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PMPT_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | zzzdelete |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PMPT_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | VentValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | BypassValve | Bypass Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR1 | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_Extension_Blanket_V1:AOI | UDT_PRS |  | AA_PRS_Extension_Blanket_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_RCH_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VentValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPumpInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | PressureVentHDR | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacHDR | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | CoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | CoolWaterOutletTemp | Primary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | VacPumpInletPrs | Vac Pump Inlet Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | LocalStartPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | LocalStopPB |  | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | WaterInletValve | Pump Water Inlet Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_RCH_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_RCH_V1:AOI | UDT_PRS |  | AA_PRS_RCH_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_PRS_V1:AOI | UDT |  | uEM_PRS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacBypassValve | Primary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacBypassValve | Secondary Vacuum Bypass Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacPump | Primary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacPump | Secondary Vacuum Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | ScrubPumpRng | Scrubber Pump Running Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PressureVentHDR | Pressure Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimVacHDR | Primary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecVacHDR | Secondary Vacuum Valves Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterFlow | Primary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterInletTemp | Primary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimCoolWaterOutletTemp | Primary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimDemisterLS | Primary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterFlow | Secondary Chiller Cooling Water Flow | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterInletTemp | Secondary Chiller Cooling Water Inlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecCoolWaterOutletTemp | Secondary Chiller Cooling Water Outlet Temperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecDemisterLS | Secondary Vacuum Pump Demister Low Level Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimHOA_InAuto_FS | Primary HOA Switch In Auto | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | PrimHOA_InHand_FS | Primary HOA Switch In Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecHOA_InAuto_FS | Secondary HOA Switch in Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | SecHOA_InHand_FS | Secondary HOA Switch In Hand | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_PRS_V1:AOI | VesselPrs | Vessel Pressure | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | Open_FS | Open Field Switch | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_PRS_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_PRS_V1:AOI | UDT_PRS |  | AA_PRS_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_QC_V1:AOI | UDT |  | uEM_QC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QC_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QC_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Blank_String |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | PhaseStartDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | DelayPreset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QC_V1:AOI | PromptTmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_QD_V2W_M2S_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | InletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | OutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | DischargeValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Quadro |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Meter |  | uCM_MET_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | Scale |  | uCM_WS_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | OperLight |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | QUADRO_PB | Pushbutton at the $NQuadro Station | uCM_DIN_V5 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HDR4_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | SourceInfo | SourceInfo Table | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | SourceProp | SourceProp Table | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_QD_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | UDT_DLY |  | AA_DLY_MP4_V4 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | FlushTarget |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | ONSFlushTarget1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | ONSFlushTarget2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Flash_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Flash |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | tmrMaxFlushTime |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | QuadroFlushing |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | Internal_OperLight |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_QD_V2W_M2S_V3:AOI | FlushComplete |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_AOD_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SourcePump |  | uCM_AOD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_AOD_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_M2S_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SourcePump |  | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_M2S_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RECIRC_V2W_VFD_V3:AOI | UDT |  | uEM_RECIRC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | TankInletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SourceOutletValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SourcePump |  | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HDR3_NOT_HELD_ON_CHASE |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | SeqNumber |  | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | IN_RMEndProcess | RM End Process Is Required | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RECIRC_V2W_VFD_V3:AOI | UDT_DLY |  | AA_RECIRC_AOD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_RSC_MGR_V3:AOI | IN_USE | Resource is in use by some equipment | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | IN_QUEUE | Resource Request Exists for this Equipment | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | UDT |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | Devices |  | EM_RSC_MGR_DEVICE_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | ProdLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_RSC_MGR_V3:AOI | CFG_MAX_ID | MAXIMUM ID NUMBER | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_CNTR_1 | Counter to Check if Request Already in queue | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_REQUEST_QUEUE |  | DINT[100] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_POS_OF_REQ_IN_QUEUE |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FIFO_CONTROL | LOAD AND UNLOAD QUEUE | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FFU_DEST | Unload Destination for FIFO | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_REQUEST_QUEUE_BUFFER |  | DINT[100] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_CONTROL_1 | LOAD SEARCH | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_STEP_1 | LOAD | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_Ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.0
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.1
COMMENT | EM_RSC_MGR_V3:AOI | WRK_Ons | oneshot |  | WRK_Ons.2
TAG | EM_RSC_MGR_V3:AOI | WRK_SEQ_BIT |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_CONTROL_2 | UNLOAD SEARCH | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_STEP_2 | CLEAR | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FAL_CONTROL_1 | CLEAR$NQUEUE | CONTROL |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_2_COPY_LENGTH |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_FSC_COPY_FROM_POS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | WRK_BIT |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
COMMENT | EM_RSC_MGR_V3:AOI | WRK_BIT | BANG BIT |  | WRK_BIT.0
TAG | EM_RSC_MGR_V3:AOI | CFG_MAX_QUEUE | MAXIMUM NUMBER IN QUEUE | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | EM_RSC_MGR_V3:AOI | StateNumberRef | State Ref to determine if state has Changed | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | StateChange | State Had Changed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | REST_DEVICE |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | REST_CONTROL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | RESET_DEVICES |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | PathTime | Minimum Time $Nthe Current Path$Nmust be maintained $Nbefore moving to next Path | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | OUT_DEVICES_DINT_FM |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | OUT_DEVICES_DINT |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Index |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | IN_DEVICES_DINT |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | HOLD_DEVICES |  | DINT[6] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | FaultTime | MaxiumumTime $Nthe Current Path$Nmay be executed$Nbefore moving to next Path | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | DeviceOutput_PathMet |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | CMP_CONTROL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Test_Pos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | BLANK_Mask |  | EM_RSC_MGR_DEVICES_LIST_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | LastUsedInstruction |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | PathSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SourceIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | LoopIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | EnableSearch |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SearchSource |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | clearindex |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SearchItem |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SourceDone |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | DelaytoDisable |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | CurrentUserRef |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | SubQueueSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QueueUserID |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QLoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QResetONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | QReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringDestinationPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringTankNumber |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locLengthDifference |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringAltPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStartPos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringSourceIndex |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_RSC_MGR_V3:AOI | locStringSource |  | STRING |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_STATUS_V1:AOI | UDT |  | uEM_STATUS_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_BottomValveClosed | Tank Bottom Valve Closed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_Weight |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_Temp |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | PreventNewOrder | Prevent New Order From Loading | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | BypassDropBit | Bypass The Internal Drop Bit | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | EM_DLY |  | uEM_DLY_V4[120] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_Cont_DLY |  | uEM_CONT_DLY_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | EM_DLY_Scale |  | uEM_DLY_SCALE_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | IN_DischPrs |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | SourceProps |  | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | SourceInfo |  | SM_SourceInfoTable_V2[40] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_STATUS_V1:AOI | DestinationLevel |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | EM_STATUS_V1:AOI | BLANK_STRING82 |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Major |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Minor |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | Ext |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExtReal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | FP |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | UDTVer |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DLYIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Status | Bits$N0=Not Active Was Not Active$N1=Active, Reset When Complete | BOOL[416] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | OneSec |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_VAL_Active |  | REAL[385] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_VAL_ActiveTotal |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | SourceTankInst |  | SM_SourceTankValidate_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DLYIndex1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | EM_DLY_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ContDlyCompleteONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | ONS | One-Shots | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | XferIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | DlyScaleCompleteONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | UseDLYForStartTimer |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_STATUS_V1:AOI | MessageResetDelay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPJK_V1:AOI | UDT |  | uEM_TEMPJK_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SteamInlet | Steam Supply$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | WaterPump | Water Supply Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRM |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV1 | Safe State Valve 1 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV2 | Safe State Valve 2 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV3 | Safe State Valve 3 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV4 | Safe State Valve 4 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV5 | Safe State Valve 5 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV6 | Safe State Valve 6 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV7 | Safe State Valve 7 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOnV8 | Safe State Valve 8 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV1 | Safe State Valve Off 1 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV2 | Safe State Valve Off 2 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV3 | Safe State Valve Off 3 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV4 | Safe State Valve Off 4 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV5 | Safe State Valve Off 5 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | SafeStateOffV6 | Safe State Valve Off 6 | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPJK_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | UDT_TEMPJK |  | AA_TEMPJK_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPJK_V1:AOI | locSafeState |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V1:AOI | UDT_TEMPC |  | AA_TEMPVC_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_V2:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Pump | Inlet Pump | uCM_M2S_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_V2:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_V2:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_V2:AOI | UDT_TEMPC |  | AA_TEMPVC_V2 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_TEMPVC_VFD_V1:AOI | UDT |  | uEM_TEMPVC_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Inlet_V2W | Inlet 2-Way Valve | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Inlet_VPR | Inlet$NProportional Valve | uCM_VPR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Pump | Inlet Pump | uCM_VFD_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | HDR | Valve Header | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Level | Level In Tank$Nfrom 0-100% | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | PrimaryRTD | Primary RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | BackupRTD | Backup RTD $NTemperature | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_TEMPVC_VFD_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | tmrAutoRestartFail |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | tmrAutoRestart |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ElapsedTime |  | ConvertToElapsedTime |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | locAutoRestartVerify |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | locAutoRestartInit |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInDeadband |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInNoCool |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInNoHeat |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevInOneShot |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PrevSetpoint |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | JacketCoilsRMPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | JacketCoilsRMReady |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | HDRsRelease |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | onsChangePath |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | CM_ExternalFault |  | SM_ExternalFaultResolve_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExternalBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | UDT_TEMPVC |  | AA_TEMPVC_VFD_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | EM_TEMPVC_VFD_V1:AOI | PumpVFD |  | uCM_VFD_V3 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EM_VENT_V2W_V1:AOI | UDT |  | uEM_VENT_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | SourceValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ScrubValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | BypassValve |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | IDLE | Module is in IDLE State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | RUNNING | Module is in Running State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | COMPLETE | Module Completed when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | FAULTED | Module is presently Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | HELD | Module is in Held State | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ABORTED | Module Aborted when last Run | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | ModuleRef |  | uSM_GLB_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EM_VENT_V2W_V1:AOI | UDT_VENT |  | AA_VENT_V1 |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EP_Ctrl_V2:AOI | UDT |  | uEP_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EP_Ctrl_V2:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EP_Ctrl_V2:AOI | ONS |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | Minor |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | Major |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EP_Ctrl_V2:AOI | FP |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | EX_REQ_V3:AOI | UDT |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | EX_REQ_V3:AOI | ons |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_Offset |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_Size |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Breakpoint_LoopCnt |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | tmrCompleteACK |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1Confirmed | HDR1 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2Confirmed | HDR2 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3Confirmed | HDR3 is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | OutletValveConfirmed | Outlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | InletValveConfirmed | Inlet Valve is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | PumpConfirmed | Pump is In Use and Confirmed | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2PrevState | Header 2$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR2Ready | Header 2$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3PrevState | Header 3$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR3Ready | Header 3 $NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1PrevState | Header 1$NPrevious State | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | HDR1Ready | Header 1$NIs Ready | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | tmrFaultReset |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | onsZoneFltReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FltActive |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FltLockOut |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | FaultCodeHolding |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | ModuleStatus |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | EX_REQ_V3:AOI | onsCfg |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibAnalog_Input:AOI | Alarm_Ack | All Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_Disable_Req | Disable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Alarm_Enable | Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_Enable_Req | Enable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Alarm_HI | HI Level Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_HIHI | HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_LO | LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Alarm_LOLO | LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | FAULT | Analog Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | FAULT_STS | Analog Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Analog_IN | Scaled Input from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Analog_Val | HMI Display Value | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibAnalog_Input:AOI | Level_HI_Stpt | Level for HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_HIHI_Stpt | Level for HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LO_Stpt | Level for LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LOLO_Stpt | Level for LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibAnalog_Input:AOI | Level_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | LibAnalog_Input:AOI | Level_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libFM:AOI | Alarm_Ack | All Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Enable | Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Enable_Req | Enable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Alarm_Disable_Req | Disable Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Alarm_HI | HI Level Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_HIHI | HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_LO | LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_LOLO | LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Alarm_Totalizer | Totalizer Not Totalizing Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | FAULT | Meter Fault | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | FAULT_STS | Meter Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Reset | Meter Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Total_Enbl | Totalizer is Installed | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Was_Reset | Meter Was Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Status_Word_1 | Flow Meter Status Word #1 | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | libFM:AOI | Status_Word_2 | Flow Meter Status Word #2 | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | libFM:AOI | Analog_IN | Scaled Input from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density | Density Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Drive_Gain | Drive Gain Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Level_HIHI_Stpt | Level for HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_HI_Stpt | Level for HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LO_Stpt | Level for LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LOLO_Stpt | Level for LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temperature | Temperature Value | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Total_IN | Totalizer from Field | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Totalizer | Totalizer Display Value | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Rate | Flow Rate | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libFM:AOI | Zero_SP | Zero Limit Value SP | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_HI_Stpt | Density Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_HIHI_Stpt | Density Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_LO_Stpt | Density Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_LOLO_Stpt | Density Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_HI | Density Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_HIHI | Density HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_LO | Density LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Density_Alarm_LOLO | Density LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_HI | Temperature Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_HIHI | Temperature HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_LO | Temperature LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_Alarm_LOLO | Temperature LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Temp_HI_Stpt | Temperature Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_HIHI_Stpt | Temperature Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_LO_Stpt | Temperature Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Temp_LOLO_Stpt | Temperature Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_HI | Drive Gain Hi Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_HIHI | Drive Gain HIHI Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_LO | Drive Gain LO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_Alarm_LOLO | Drive Gain LOLO Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_HI_Stpt | Drive Gain Setpoint For HI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_HIHI_Stpt | Drive Gain Setpoint For HIHI Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_LO_Stpt | Drive Gain Setpoint For LO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Drive_Gain_LOLO_Stpt | Drive Gain Setpoint For LOLO Alarm | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libFM:AOI | Level_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Level_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Level_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Alm_Total_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Total_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Total_Storage |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Density_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Density_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Temp_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Temp_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_HI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_HIHI_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_LO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_LOLO_Delay_Setpoint |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libFM:AOI | Drive_Gain_HI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_HIHI_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_LO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libFM:AOI | Drive_Gain_LOLO_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libHOA:AOI | IN_AUTO | HOA In Auto | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | IN_HAND | HOA In Hand | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | IN_OFF | HOA In Off | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_AUTO | HOA Auto Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_HAND | HOA Hand Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | HOA_Pos_Flt | HOA Not In Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libHOA:AOI | MODE | HOA Mode$N1 = Hand and Auto$N2 = Hand Only$N3 = Auto Only | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibLvl_Switch:AOI | Alarm_Ack | All Level Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Alarm_Disable_Req | Disable Level Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Alarm_Enable_Req | Enable Level Alarming | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Alarm_HLS | High Level Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Alarm_LLS | Low Level Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | FAULT_STS | Device Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | FAULT | Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | HLS_Alarm_Enable | High Level Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LLS_Alarm_Enable | Low Level Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSH_INPUT | Level Switch High Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSL_INPUT | Level Switch Low Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | LSH_STS | Level Switch High Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | LSL_STS | Level Switch Low Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibLvl_Switch:AOI | Level_HLS_Delay_Setpoint | High Level Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Level_LLS_Delay_Setpoint | Low Level Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibLvl_Switch:AOI | Level_HLS_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | LibLvl_Switch:AOI | Level_LLS_Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libMtr_Simulation:AOI | Create_Running_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libMtr_Simulation:AOI | Energize_IN |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libMtr_Simulation:AOI | Running_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libMtr_Simulation:AOI | RunTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libPump_Mtr:AOI | ALARM_ACK | Clear Device Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | AUTO_ACTIVATE | Auto Activation of Pump If Pump Is In Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | DISC_OK | Motor Disconnect Okay | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ENERGIZE | Pump Coil Energize to Field Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | FAULT | Pump Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FAULT_STS | Pump Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | FIELD_ACTIVATE | Field Activation Of Pump If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FlowReset | Reset Flow Total | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | HMI_Field | HMI Field Selected | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | INTERLOCK | Prevent the Motor from operating$N(1 = OK) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_BYPASS | Interlock Bypass$N(0 = No 1 = Yes $NOnly Functional if Bypassable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_BYPASSABLE | Allow Interlock Bypassing$N(0 = No 1 = Yes) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_ENABLED | Interlock Is OK Has Been Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_OK | Device Interlocks OK | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_RESET | Interlock Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | INTLK_RST_RQRD | Interlock Reset Required | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | LIMIT_OVR | Input Limit Switch Override | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | MAN_ACTIVATE | Manual Activation Of Pump If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | MAN_CMD_STS | Set from HMI Auto = 0 | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | OFFDLYDSBLE | Off Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | OFF_ONS | Off One-Shot | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | OFF_STS | Pump is Off | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Pump | Device is a Pump | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUN_ONS | Run One-Shot | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | RUNDLYDSBLE | Run Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNNING_LIMT | Pump Running Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNNING_STS | Pump is Running | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalFlowAlarm | Motor Flow is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeAlarm | Motor Hours is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeReset | Cumulative Run Time Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TRANSITION | Pump Is Starting or Running Limit not On | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | VFD_Fault | VFD Faulted | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | VFD_RESET | VFD Fault Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ACTVT_OUT1 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | ACTVT_OUT2 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FaultCode | Fault Code From Drive | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Intlk_Dly | Interlock Delay Time | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | INTLK_TYPE | Interlock Type$N( 0 = Force Stop 1 = Force Start) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | ModeType | 0=Auto & Manual Mode$N1=Auto Mode$N2=Manual Mode | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libPump_Mtr:AOI | OFFPreset | Off Time Preset | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | RUNPreset | Run Time Preset | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | TotalFlowSP | Cumulative Flow Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalHrSP | Cumulative Run Time Hours Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Current | Motor Current | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | FlowTotal | Total Flow | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_1 | Flow Meter Input #1 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_2 | Flow Meter Input #2 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_3 | Flow Meter Input #3 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_4 | Flow Meter Input #4 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Meter_IN_5 | Flow Meter Input #5 | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Pressure | Motor Pressure | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Spd_Cmd | Speed Command | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Spd_Max | Maximum Motor Speed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Spd_Min | Minimum Motor Speed | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Spd_Output | Speed Output | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libPump_Mtr:AOI | Temperature | Motor Temperature | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | TotalTimeHrs | Cumulative Run Time Hours | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | PERMISSIVE_OK | Permissive To Operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Field_Start_PB | Field Start Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | Field_Stop_PB | Field Stop Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libPump_Mtr:AOI | OFF_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | RUN_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | AUTO_ONS |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | CurrentHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | TemperatureHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | CurrentHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | TemperatureHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libPump_Mtr:AOI | PressureHiFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureHiLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalTimer | Cumulative Run Time 1 Hour Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalHrsStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureLoFault |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureLoLimit |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | PressureDly |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | LoPrsEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalAddedCur | Total Current Amount Added | REAL[6] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | FlowONS | ONE-SHOT | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Meter_Prev |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | TotalAddedPrev |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Meter_Mont |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | FlowStore |  | REAL[5] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiPrsEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiCurrentEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | HiTempEnable |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | Intlk_Dly_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | VFD_RESET_TMR |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | VFD_RESET_SP | VFD Reset On Time SP | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libPump_Mtr:AOI | RunDlyOff |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | LibSwitch:AOI | Alarm_Ack | All Switch Alarm Ack | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | Alarm | Switch Alarm | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | LibSwitch:AOI | FAULT_STS | Device Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | FAULT | Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | Alarm_Enable | Switch Alarming Enabled | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | INPUT | Switch Input$N(0 = in Alarm) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | LibSwitch:AOI | STS | Switch Status To HMI | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | LibSwitch:AOI | Delay_Setpoint | Switch Alarm Delay | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | LibSwitch:AOI | Delay |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libValve_ACT_SOL:AOI | ALARM_ACK | Clear Device Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | AUTO_ACTIVATE | Auto Activation of Valve If Valve Is In Auto Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_FLT | Valve Closed Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_ONS | Close ONS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_STS | Valve in the Closed Postion | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSED_LIMT | Closed Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CLSDLYDSBLE | Close Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CycleReset | Cycle Count Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CycleCntAlarm | Cycle Count Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ENERGIZE | Valve Coil Energize to Field Output | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | FAULT | Valve Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FAULT_STS | Valve Fault Status to HMI | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | FIELD_ACTIVATE | Field Activation Of Device If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FlowReset | Reset Flow Total | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | INTERLOCK | Interlocks required for the device to operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_BYPASS | Interlock Bypass$N(0 = No 1 = Yes $NOnly Functional if Bypassable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_BYPASSABLE | Allow Interlock Bypassing$N(0 = No 1 = Yes) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_ENABLED | Interlock Is OK Has Been Reset | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_OK | Device Interlocks OK | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_RESET | Interlock Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | INTLK_RST_RQRD | Interlock Reset Required | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | HMI_Field | HMI Field Selected | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | LIMIT_OVR | Limit Switch Override | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | MAN_ACTIVATE | Manual Activation Of Valve If Manual Mode | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | MAN_CMD_STS | Auto/Man Device Status 1=Man | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_FLT | Valve Opened Fault | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_LIMT | Open Limit Switch | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | OPEN_ONS | Open ONS | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | OPEN_STS | Valve in the Open Position | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | OPNDLYDSBLE | Open Delay Timer Override Disable | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | SolPump | Device is a Pump | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | TotalFlowAlarm | Motor Flow is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeAlarm | Pump Hours is Greater Than Or Equals Setpoint Alarm Maintenance | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeReset | Cumulative Run Time Reset | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TRANSITION | Valve Is Moving Or Not At The Final Position | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ACTVT_OUT1 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number Bits 0-31 | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ACTVT_OUT2 | Blending Activate By Mixer Node Number Raw Material Activate by Node Number Bits 32-63 | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | ClosePreset | Amount of Seconds for Valve to Close | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | CountSP | Cumulative Cycle Count Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CycleCount | Cumulative Cycle Counter | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | DeviceType | 0=No Limit 1=Closed Limit 2=Opened & Closed Limits | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | Intlk_Dly | Interlock Delay Time | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | INTLK_TYPE | Interlock Type$N( 0 = Force Close 1 = Force Open) | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | ModeType | 0=Auto & Manual Mode 1=Auto Mode$N2=Manual Mode | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_ACT_SOL:AOI | OpenPreset | Amount of Seconds for Valve to Open | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_ACT_SOL:AOI | TotalFlowSP | Cumulative Flow Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalHrSP | Cumulative Run Time Hours Operator Notification Setpoint | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | FlowTotal | Total Flow | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Meter_IN | Flow Meter Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | TotalTimeHrs | Cumulative Run Time Hours | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | PERMISSIVE_OK | Permissive To Operate | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Field_Open_PB | Field Open Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | Field_Close_PB | Field Close Push Button | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | libValve_ACT_SOL:AOI | CLOSE_TMR | Closing Timer | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | OPEN_TMR | Opening Timer | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | AUTO_ONS | Auto ONS | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_ACT_SOL:AOI | CYCLE_ONS | Cycle One-shot | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | FlowONS | ONE-SHOT | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalAddedCur | Total Current Amount Added | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | FlowStore |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalAddedPrev |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Meter_Mont |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Meter_Prev |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalTimer | Cumulative Run Time 1 Hour Timer | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | TotalHrsStorage |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | Intlk_Dly_Tmr |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | libValve_ACT_SOL:AOI | CloseDly |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | libValve_Simulation:AOI | Close_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | Create_Close_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_Simulation:AOI | Create_Open_Fault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | libValve_Simulation:AOI | Energize_IN |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | Open_Limit |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | libValve_Simulation:AOI | CloseTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | libValve_Simulation:AOI | OpenTimer |  | TIMER |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | MM_CIR_V1:AOI | UDT |  | uMM_CIR_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IndirectUserID | Indirect Using In Use By Registers | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IndirectUserType | Indirect Using In Use By Type Registers | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseA | Raw PhaseA Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseB | Raw PhaseB Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | IN_RawPhaseC | Raw PhaseC Current Input | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | InHealth_Current | Input Health Current Input | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | InUseByLink | Production Area Linking Data | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | MM_CIR_V1:AOI | STS_Enabled | MM Is Enabled | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_Faulted | MM Is Faulted | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_SIM | Simulation Mode Is Active | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | STS_SuppressAlarms |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | MM_CIR_V1:AOI | IN_SuppressAlarms |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | MM_CIR_V1:AOI | IN_DisableIndirectUse | Disable The IndirectUsing Instruction | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | MM_CIR_V1:AOI | FP | FacePlate Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | UDTVer | UDT Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Minor | Minor Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Major | Major Rev | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | Ext | Extended Rev Notes | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | ExtReal | Extended As Real | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locOffTooLong |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locWaitInRangeTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locIndirectUserID |  | DINT[2] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locWaitMinOnTime |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | locIndirectUsingAOI |  | SM_IndirectUsing_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | onsMaxTimeOFF |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | MM_CIR_V1:AOI | onsAutoResetSFTimeOff |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Receive_V2W_V1:AOI | UDT_V2W |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | EX_REQ |  | uEX_REQ_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | pc_IN_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | pc_OUT_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | PC_ConnStat | Produced/Consumed Connection Status 1=Good | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | COMMS_OK |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | ACTIVE |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | PC_Receive_V2W_V1:AOI | AOI_EX_REQ |  | EX_REQ_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_InUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_MaxInUseSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_InUseWritePos |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Receive_V2W_V1:AOI | loc_NoInUseOverrun |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | PC_Send_V2W_V1:AOI | UDT_V2W |  | uCM_V2W_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | pc_IN_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | pc_OUT_V2W |  | PC_Remote_CM_V2W |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | PC_ConnStat | Produced/Consumed$NConnection Status | BOOL |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | InUseByLink |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | PC_Send_V2W_V1:AOI | CM_UDT_V2W |  | CM_V2W_V3 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | SM_RequestUse_Open |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | SM_RequestUse_Close |  | SM_RequestUse_V1 |  | (Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | loc_InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | PC_Send_V2W_V1:AOI | loc_InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_AutoCMDMan_V1:AOI | IN_Auto |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_AutoCMDMan_V1:AOI | Secondary | Secondary CMD Input - (DINT[0] > 0) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Average:AOI | NumOfItems | Number to Points to Average | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Average:AOI | LOAD_AVG |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Average:AOI | Average_OUT |  | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Average:AOI | UNLOAD_AVG |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Average:AOI | Average_Array |  | REAL[20] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Average:AOI | Average_CTL |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | SM_Average:AOI | Average_CTL_2 |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_BCDMonitor_V1:AOI | Bit0 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit1 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit2 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | Bit3 |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_BCDMonitor_V1:AOI | BCDValue |  | INT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CC_V3:AOI | UDT |  | uSM_CC_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CC_V3:AOI | tmrCMDRec |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CHAR_V1:AOI | Char |  | uSM_CHR |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CHAR_V1:AOI | HEADER_B | File Header Labels for CM Routines Bxx | BOOL[32] |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_PROC_HIGH_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_PROC_LOW_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_MULT_HIGH_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TAG | SM_CHAR_V1:AOI | CHR_MULT_LOW_VALUE |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_ChaseWaterValve:AOI | HDR1 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR2 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR3 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR4 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR5 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR6 |  | uEM_RSC_MGR_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_ChaseWaterValve:AOI | HDR1InService | Header 1 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR2InService | Header 2 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR3InService | Header 3 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR4InService | Header 4 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR5InService | Header 5 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR6InService | Header 6 In Service | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR1_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR2_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR3_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR4_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR5_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | HDR6_OpenChaseValve |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_ChaseWaterValve:AOI | ActiveHDRIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | priorityindex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | CountSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | CountMax |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | PrimaryHDRPriority |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | initalscancomplete |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | PreviousPriority |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ChaseWaterValve:AOI | NoChaseActive | No Chase Is Currently Active$NOpen All Chase Valves | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_A |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_B |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_CMDAutoOR_V1:AOI | AutoCMD_Dest |  | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Count_V1:AOI | IN_Pulse |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | OUT_Count |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | IN_Stopped | Accummulate Pulses When Not Stopped. Reset Counter When Stopped | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | ZoneLink |  | CM_ZON_LNK_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Count_V1:AOI | Enable |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Count_V1:AOI | Counter |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Count_V1:AOI | IN_Pulse_ons |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_ExternalFaultResolve_V1:AOI | FaultWord |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | LastInternalFaultBit |  | INT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | FaultBitOutput |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | ExternalFault |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_ExternalFaultResolve_V1:AOI | FaultBit |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_ExternalFaultResolve_V1:AOI | ActiveFault |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_HoseConnect_V1:AOI | HoseConnect |  | uSM_HoseConnect_V1[10] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | UDT |  | uSM_HoseConnect_V1 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SourcePath |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | AltPath |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | UserBitID |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SEQIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | SEQ_FD |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | InputDevices |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | Mask |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | OutputDevices |  | DINT |  | (RADIX := Binary, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | STS_Faulted |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_HoseConnect_V1:AOI | locSEQSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSEQIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strSource |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strAltPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | strSourcePath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locLoopIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSearchValue |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locSEQPath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locMask |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | locStatus |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | OP1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | OP2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | L9_P1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | L9_P2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_OP1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_OP2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_L9_P1 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | Search_L9_P2 |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HoseConnect_V1:AOI | IndexEqual |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_HosePreact:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | FlowrateThreshold | Flowrate is above this Threshold, Use System Preact. Othewise Use Hose Preact | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | TimeToClose | Inlet Valve Time to Close | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_HosePreact:AOI | FRFactor | Multipler to Flowrate Adjustment | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_HosePreact:AOI | HosePreact |  | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_HosePreact:AOI | CurrentFlowrate |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | SourceInfoPreact |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | onsCapturePreact |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | LowFlow |  | TIMER |  | (Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | UseFixedPreact |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_HosePreact:AOI | PreactTemp |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | EM_AGIT |  | uEM_AGIT_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectEMAgit_V1:AOI | DisableIndirect | Disable Indirect Using | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | PrevInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | PrevInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectEMAgit_V1:AOI | InUseByType1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_IndirectUsing_V3:AOI | InUseBy |  | DINT[2] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectUsing_V3:AOI | AutoEnable |  | DINT[17] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_IndirectUsing_V3:AOI | DisableIndirect | Disable Indirect Using | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := false)
TAG | SM_IndirectUsing_V3:AOI | InUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | InUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | PrevInUseBy0 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_IndirectUsing_V3:AOI | PrevInUseBy1 |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Interlock_V1:AOI | IN_Interlock |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_Fout | Secondary CMD Input - (DINT[0] > 0) | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_IlkBypass |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | OUT_Sts_Interlocked |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Interlock_V1:AOI | CMD_ResetFault |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | IN_FLT_Interlock |  | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := true, Visible := true)
TAG | SM_Interlock_V1:AOI | Not_Bypassed |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_InUseByUsing_V3:AOI | InUseByIndex | In Use By Array Index | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeID | Module Reference Type ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeIndex | Module Type Index | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyTypeArrayRef | Module Array Ref | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyBitID |  | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | MyModuleStatus | Module Status Information | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UsingArray |  | uSM_InUseBy_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeID | Type ID Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeIndex | Type Index Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserPriority | Fast Track Priority Level (1=Highest) | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read/Write, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | ER | Error Status Bit | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | FL | Module Array Of Current User Is Full | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | DN | Done Status Bit | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | UserTypeArrayRef | Type Array Reference Of Module Using This Module | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_InUseByUsing_V3:AOI | GlobalID | The Calculated Global ID | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousUsedBy | InUseBy Value of Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | FSC_Ctrl |  | CONTROL |  | (Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousGlobalID | Global ID From The Previous Scan | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | PreviousCount | Determine Count Previous Entry Count | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | CopyLen | Length Required To Move Data | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | Count | Count From InUseBy List | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | MaxUsing | Maximum Users Configured In System | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | MaxModules | Maximum Modules Allowed To Be Used | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | CopyStartPosition | Copy Array First Position | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_InUseByUsing_V3:AOI | UserBitID | Bit ID Of Used Object (Not Applicable to CMs) | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_MessageGroupMember_V1:AOI | EnableMSG | End Point Device Is In Use | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | TokenTag | Group Token Tag | DINT |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | MyID | My Group Token ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | NextID | Next Group Token ID | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read Only, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | Message |  | MESSAGE |  | (Usage := InOut, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | MSGConfigs |  | SM_CIPMsg_V1[5] |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | CurrentResultIndex | Index Of Current Result | INT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_MessageGroupMember_V1:AOI | STS_Processing |  | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_MessageGroupMember_V1:AOI | locMSGIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locProcessing |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locMSGSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | locLastPass |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | onsDone |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_MessageGroupMember_V1:AOI | onsNext |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_Preact:AOI | DLY |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_Preact:AOI | PreactAdjMinAddThreshold | Minimum Addition Setpoint to Allow for Preact Adjustment$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | PreactFlowAdjEnable | Preact Flow Adjustment Enable/Disable$N(1 = Enable) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | CalcPreactTimeAdj | Calculated Prect Time Adjustment | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | CalcPreactErrAdjust | Calculated Preact Error Adjustment$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | MaxPreactTime | Maximum Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinPreactTime | Minimum Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MaxPreact | Maximum Preact Setpoint$N(Lbs.) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinPreact | Minimum Preact Setpoint$N(Lbs) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | ErrPercent | Error Percent For Last Addition$N(%) | REAL |  | (RADIX := Float, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := false)
TAG | SM_Preact:AOI | PreactAdjustPercent | Preact Adustment Percent Setpoint$N(%) | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | PreactEnable | Enable/Disable Auto Preact Adjustment$N(1 = Enabled) | BOOL |  | (RADIX := Decimal, Usage := Input, ExternalAccess := None, Required := false, Visible := true)
TAG | SM_Preact:AOI | MinFlowRateSP | Minimum Flow Rate for Preact Calculations | REAL |  | (RADIX := Float, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := true)
TAG | SM_Preact:AOI | Index | Array Position | DINT |  | (RADIX := Decimal, Usage := Input, ExternalAccess := Read/Write, Required := false, Visible := false)
TAG | SM_Preact:AOI | CurrentFlowrate |  | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | onsCaptureError |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | FlowLbPerSecStore | Stored Flow Rate While System Running | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | AdditionErrorSample | Addition Error For Preact Adjustment Sample Number | REAL[4] |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | UpdatePreactCalcs | Update Preact Calculation | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | AdditionAvgError | Addition Average Error for Preact Adjustment | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | PreactAdjustCmd | Preact Adjustment Command | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | PreactTimeSP | Preact Time Setpoint$N(Sec) | REAL |  | (RADIX := Float, Usage := Local, ExternalAccess := Read Only)
TAG | SM_Preact:AOI | onsReset |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | MissCharge |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_Preact:AOI | EID |  | STRING_20 |  | (Usage := Local, ExternalAccess := Read/Write)
TAG | SM_Preact:AOI | DESC |  | STRING_40 |  | (Usage := Local, ExternalAccess := Read/Write)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_RequestUse_V1:AOI | IN_AutoReq | Auto Request Array | DINT[39] |  | (RADIX := Decimal, Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_RequestUse_V1:AOI | DelayEnableOut |  | BOOL |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_SourceTankValidate_V3:AOI | SourceInfo |  | SM_SourceInfoTable_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceProp |  | SM_SourceData_V2 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | UDT |  | uEM_DLY_V4 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceMES | Source Tank from MES | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourceInfoStorageIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourcePropIndex |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SourcePath | Source AltPath | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | TankPath | Destination AltPath | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | Storage_FD | Found In Source Info Storage | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | SP_FD | Found In Source Properties | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | DN | Read Full Array | BOOL |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := false, Visible := true)
TAG | SM_SourceTankValidate_V3:AOI | ListSize | Max Size Of Lookup List$N | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | LoopIndex | Loop Index Value | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SearchTank | Tank To Lookup$N | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SourcePropSize |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SourceInfoTable |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | DeliveryEMInfo |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | SearchValue |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | locDeliveryEMInfoIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | locSourcePropIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | locSourceInfoStorageIndex |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := Read Only)
TAG | SM_SourceTankValidate_V3:AOI | strSource |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strAltPath |  | STRING_10 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strSourcePath |  | STRING_20 |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | locSourcePath |  | DINT |  | (RADIX := Decimal, Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strMyTankNumber |  | STRING |  | (Usage := Local, ExternalAccess := None)
TAG | SM_SourceTankValidate_V3:AOI | strMyTankNumberPath |  | STRING |  | (Usage := Local, ExternalAccess := None)
TYPE | SCOPE | NAME | DESCRIPTION | DATATYPE | SPECIFIER | ATTRIBUTES
TAG | SM_WEP_UnloadRangeCheck_V1:AOI | LI_As_AIN |  | uCM_AIN_V3 |  | (Usage := InOut, Constant := false, Required := true, Visible := true)
TAG | SM_WEP_UnloadRangeCheck_V1:AOI | LevelToUnload |  | DINT |  | (RADIX := Decimal, Usage := Output, ExternalAccess := Read Only, Required := true, Visible := true)
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SystemFaults | B01_SF_T981 | System fault if Retention Tank Level is High | OTE(SF_T981.SET.SIM_ON) | 0
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | System_Status | CLx_Status | ALARMS FOR LOCAL RACK AND REMOTE RACKS | OTE(CLx_SysStatus.Remote_7_CommFault) | 28
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_CoFeed_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_CoFeed_V3:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_CoFeed_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 8
RCOMMENT | AA_CoFeed_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 13
RCOMMENT | AA_CoFeed_V3:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 16
RCOMMENT | AA_CoFeed_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 49
RCOMMENT | AA_CoFeed_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 50
RCOMMENT | AA_CoFeed_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 51
RCOMMENT | AA_CoFeed_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_CoFeed_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 70
RCOMMENT | AA_CoFeed_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Monitor Deliveries To Determine If Either Delivery Is a Co-Feed & Issue The Start Command$N | OTL(UDT.CMD.Start) | 87
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Restart From Held$N | OTL(UDT.CMD.Start) | 88
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Go To Holding States When One Of The Active Deliveries Go To Held$N | OTL(UDT.WRK.UserHold) | 89
RCOMMENT | AA_CoFeed_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 175
RCOMMENT | AA_CoFeed_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 176
RCOMMENT | AA_CoFeed_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 179
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_CoFeed_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_CoFeed_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_CoFeed_V4:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 8
RCOMMENT | AA_CoFeed_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 13
RCOMMENT | AA_CoFeed_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 16
RCOMMENT | AA_CoFeed_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 49
RCOMMENT | AA_CoFeed_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 50
RCOMMENT | AA_CoFeed_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 51
RCOMMENT | AA_CoFeed_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_CoFeed_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 70
RCOMMENT | AA_CoFeed_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Monitor Deliveries To Determine If Either Delivery Is a Co-Feed & Issue The Start Command$N | OTL(UDT.CMD.Start) | 87
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Restart From Held$N | OTL(UDT.CMD.Start) | 88
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Go To Holding States When One Of The Active Deliveries Go To Held$N | OTL(UDT.WRK.UserHold) | 89
RCOMMENT | AA_CoFeed_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 177
RCOMMENT | AA_CoFeed_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 178
RCOMMENT | AA_CoFeed_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 181
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Monitor When Source Has Changed | OTL(UDT.WRK.SourceTankChanged) | 5
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Monitor When Alternate Path Has Changed | OTL(UDT.WRK.AltPathChanged) | 6
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Initialize Copy SourceInfo Instruction | OTU(UDT.WRK.SourceInfoStorageCopyComplete) | 7
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Verify Source & Destination Are Valid$NLoad SourceInfo & SourceProp | OTL(UDT.WRK.SourceSelected) | 8
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | TIMER PRESETS | MUL(UDT.Source.Info.PumpAllLowTime,1000,UDT.WRK.tmrPumpAllAutoEnd.PRE) | 12
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 13
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Nothing To Do$NJump To End$N | JMP(label_1) | 24
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Clear Registers When ClearSource Command Is Issued Or When AltPath Has Changed | OTU(SourceTankInst.DN) | 25
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 27
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 30
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 83
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 84
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 85
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 107
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 108
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 114
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | These Were Originally Only Allowed In State 30 But Were Moved to Allow Manipulation During Active Delivery | MOV(UDT.Source.Info.FlowSPDribble,UDT.VAL.DribbleRateSetpoint) | 145
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 323
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 324
RCOMMENT | AA_DLY_MP4_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 327
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Monitor When Source Has Changed | OTL(UDT.WRK.SourceTankChanged) | 5
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Monitor When Alternate Path Has Changed | OTL(UDT.WRK.AltPathChanged) | 6
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Initialize Copy SourceInfo Instruction | OTU(UDT.WRK.SourceInfoStorageCopyComplete) | 7
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Verify Source & Destination Are Valid$NLoad SourceInfo & SourceProp | OTL(UDT.WRK.SourceSelected) | 8
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | TIMER PRESETS | MUL(UDT.Source.Info.PumpAllLowTime,1000,UDT.WRK.tmrPumpAllAutoEnd.PRE) | 12
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 13
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Nothing To Do$NJump To End$N | JMP(label_1) | 24
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Clear Registers When ClearSource Command Is Issued Or When AltPath Has Changed | OTU(SourceTankInst.DN) | 25
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 27
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 30
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 83
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 84
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 85
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 107
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 108
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 114
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | These Were Originally Only Allowed In State 30 But Were Moved to Allow Manipulation During Active Delivery | MOV(UDT.Source.Info.PumpSpeed,UDT.VAL.PumpSpeed) | 145
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 338
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 339
RCOMMENT | AA_DLY_PMPALL_V4:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 342
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_INERT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_INERT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | AA_INERT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | AA_INERT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | AA_INERT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | AA_INERT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | AA_INERT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | AA_INERT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Path_CMD_Energize) | 65
RCOMMENT | AA_INERT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_INERT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 70
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | AA_INERT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 10
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 11
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 16
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 17
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 18
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 30
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 54
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 55
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 71
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 72
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 78
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 83
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.Mode,UDT.VAL.Mode) | 84
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 86
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 108
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 114
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 115
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1400,UDT.SET.NextStateNumber) | 116
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 117
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 118
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 122
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NPRS Cook Mode (Pressure Cook)$N**************************** | MOV(1410,UDT.SET.NextStateNumber) | 126
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | *************$NBleed Mode$N**************************** | MOV(1510,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 135
RCOMMENT | AA_PRS_Extension_Blanket_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 171
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 6
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 7
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 12
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 13
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 14
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 27
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 51
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 52
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 71
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 72
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 78
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 83
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTL(UDT.WRK.ModeChange) | 84
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 88
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 110
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 117
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 118
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NVacuum Pump Mode Selected$N*************************** | MOV(1600,UDT.SET.NextStateNumber) | 119
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 121
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 125
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *************$NVac Pump Mode$N**************************** | MOV(1610,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Control of Primary Pump | NOP() | 134
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.PrimBypassValve_CMD_Open) | 137
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 138
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NPrimary Vacuum Pump Control$N******************* | OTE(VacPump.CMD.AutoStop) | 162
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | *********$NPrimaryVacuum Pump Bypass Valve Control$N******************* | MOV(0,VacBypassValve.SET.FullRate) | 163
RCOMMENT | AA_PRS_RCH_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 176
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_PRS_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_PRS_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_PRS_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_PRS_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_PRS_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_PRS_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_PRS_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_PRS_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 57
RCOMMENT | AA_PRS_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 58
RCOMMENT | AA_PRS_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 77
RCOMMENT | AA_PRS_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 78
RCOMMENT | AA_PRS_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 84
RCOMMENT | AA_PRS_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_PRS_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.Mode,UDT.VAL.Mode) | 90
RCOMMENT | AA_PRS_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 94
RCOMMENT | AA_PRS_V1:AOI | Logic | Change Mode$N | MOV(UDT.VAL.Mode,UDT.SET.Mode) | 116
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NSeal Mode Selected$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 122
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NAtmosphere Mode Selected$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 123
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NScrub Mode Selected$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 124
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NVacuum Pump Mode Selected$N*************************** | MOV(1600,UDT.SET.NextStateNumber) | 125
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NSeal Mode$N**************************** | MOV(1110,UDT.SET.NextStateNumber) | 126
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NAtmosphere Mode$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 130
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NScrub Mode$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 134
RCOMMENT | AA_PRS_V1:AOI | Logic | *************$NVac Pump Mode$N**************************** | MOV(1620,UDT.SET.NextStateNumber) | 141
RCOMMENT | AA_PRS_V1:AOI | Logic | When Primary Pump is selected | MOV(UDT.WRK.PrimVacModePathID,UDT.WRK.HDR1_ReqPath) | 142
RCOMMENT | AA_PRS_V1:AOI | Logic | When Secondary Pump is selected | MOV(UDT.WRK.SecVacModePathID,UDT.WRK.HDR1_ReqPath) | 143
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary vacuum Header | NOP() | 145
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Pump | NOP() | 153
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.PrimBypassValve_CMD_Open) | 156
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Secondary vacuum Header | NOP() | 157
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Secondary Pump | NOP() | 161
RCOMMENT | AA_PRS_V1:AOI | Logic | Control of Primary Vacuum Proportional Valve | OTE(UDT.WRK.SecBypassValve_CMD_Open) | 163
RCOMMENT | AA_PRS_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 164
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NPrimary Vacuum Pump Control$N******************* | OTE(PrimVacPump.CMD.AutoStop) | 188
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NSecondary Vacuum Pump Control$N******************* | OTE(SecVacPump.CMD.AutoStop) | 189
RCOMMENT | AA_PRS_V1:AOI | Logic | *********$NPrimaryVacuum Pump Bypass Valve Control$N******************* | MOV(0,PrimVacBypassValve.SET.FullRate) | 190
RCOMMENT | AA_PRS_V1:AOI | Logic | Secondary Vacuum Pump Bypass Valve Control$N******************* | MOV(0,SecVacBypassValve.SET.FullRate) | 191
RCOMMENT | AA_PRS_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 205
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 3
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | OTE(UDT.WRK.NotInUse) | 23
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | Disable if not enabled | JMP(Disabled) | 24
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 28
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 38
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.Enable) | 39
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 41
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 69
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 70
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 71
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 81
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 82
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.TankInletValve_CMD_Open) | 88
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 95
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 157
RCOMMENT | AA_RECIRC_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 160
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 11
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 12
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 17
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 18
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 19
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 31
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 58
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 59
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 86
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 87
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 93
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 98
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 99
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 101
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | This was Temp Override and Overcome. This was Removed | MOV(1000,UDT.SET.NextStateNumber) | 124
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 131
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 137
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 138
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 139
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(0,UDT.WRK.ValveRequest) | 140
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(0,UDT.WRK.LastMode) | 147
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 151
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 154
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 175
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Jacket Coils Configuration | CPT(UDT.WRK.ReqPath,32) | 187
RCOMMENT | AA_TEMPJK_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 198
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 135
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | AEA - To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 151
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 153
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 157
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 162
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 183
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 189
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 190
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 191
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 192
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 193
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 194
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 195
RCOMMENT | AA_TEMPVC_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 210
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 135
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | AEA - To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 150
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1500,UDT.SET.NextStateNumber) | 152
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1500,UDT.SET.NextStateNumber) | 156
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Aborting Shut down sequence | NOP() | 161
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 182
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 188
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 189
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 190
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 191
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 192
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 193
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 194
RCOMMENT | AA_TEMPVC_V2:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 209
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 13
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 14
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 19
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 20
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 21
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 33
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 60
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 61
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | RESTARTING LOGIC$N$N*************************************************************************************************************************************************************************************************************************************************$N | MOV(1000,UDT.SET.NextStateNumber) | 89
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 90
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5105,UDT.SET.NextStateNumber) | 96
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 102
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 103
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 105
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *******************$NCalculate the Low Temperature band and High Temperature band$N$N************************************ | CPT(UDT.WRK.HiDeadband,UDT.VAL.Setpoint + UDT.VAL.Deadband) | 127
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Change Mode$N | OTL(UDT.WRK.ModeChange) | 132
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NOne-Shot Mode$N*************************** | MOV(1100,UDT.SET.NextStateNumber) | 142
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 143
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NNo-Heat Mode is Not Activated$N*************************** | MOV(1200,UDT.SET.NextStateNumber) | 144
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NNo-Cool Mode is Not Activated$N*************************** | MOV(1300,UDT.SET.NextStateNumber) | 145
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *********$NPID Control Activated$N*************************** | MOV(1500,UDT.SET.NextStateNumber) | 146
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NOne Shot Mode$N**************************** | MOV(1120,UDT.SET.NextStateNumber) | 147
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | To Complete out of Running States | MOV(6000,UDT.SET.NextStateNumber) | 152
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NNo Heat Mode is not Activated$N**************************** | MOV(1210,UDT.SET.NextStateNumber) | 154
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | *************$NNo Cool Mode$Nis not Activated$N**************************** | MOV(1310,UDT.SET.NextStateNumber) | 158
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Aborting Shut down sequence | NOP() | 163
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Running$N1000-4999 | MOV(UDT.SET.SetpointOVR,UDT.VAL.Setpoint) | 184
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of Inlet 2-way valve type$N************************************** | OTL(Inlet_V2W.CMD.AutoClose[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 190
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of Inlet Proportional valve type$N************************************** | MOV(0,Inlet_VPR.SET.FullRate) | 191
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of V2W valves | OTE(UDT.WRK.InletV2W_CMD_Open) | 192
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of V2W valves | OTL(UDT.WRK.InletVPR_CMD_Open) | 193
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of Pump | OTE(UDT.WRK.InletPump_CMD_Run) | 194
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Control of Pump | OTU(UDT.WRK.InletPump_CMD_Run) | 195
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Jacket Coils Configuration | MOV(UDT.VAL.MyTankNumber,UDT.WRK.ReqPath) | 196
RCOMMENT | AA_TEMPVC_VFD_V1:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 211
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | AA_VENT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | AA_VENT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | AA_VENT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | AA_VENT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | AA_VENT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | AA_VENT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | AA_VENT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | AA_VENT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Path_CMD_Energize) | 65
RCOMMENT | AA_VENT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 69
RCOMMENT | AA_VENT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 70
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | AA_VENT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 1
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_AIN_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | CM_AIN_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AIN_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 2
RCOMMENT | CM_AIN_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.LoTimer.PRE,1000,UDT.CFG.LoFaultTime) | 6
RCOMMENT | CM_AIN_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 7
RCOMMENT | CM_AIN_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 8
RCOMMENT | CM_AIN_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 9
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 16
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 17
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 18
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 19
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.FLT.Overrange) | 20
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.HiHi) | 21
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 22
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.LoLo) | 23
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 24
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 25
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Calibration Fault | OTL(UDT.FLT.CalFault) | 26
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Underrange | OTL(UDT.FLT.Underrange) | 27
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Overrange | OTL(UDT.FLT.Overrange) | 28
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 30
RCOMMENT | CM_AIN_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 31
RCOMMENT | CM_AIN_V3:AOI | Logic | VALUE: Analog Input | MOV(UDT.SET.SIM_Value,UDT.VAL.ActualScaled) | 34
RCOMMENT | CM_AIN_V3:AOI | Logic | VALUE: Analog Input | MOV(UDT.VAL.ActualFiltered,UDT.WRK.FilteredLast_Scan) | 35
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 39
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 40
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 5 In Use | MOV(5,UDT.VAL.HMIState) | 41
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 5 Normal Conditions Not In Use | MOV(6,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AIN_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 43
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 44
RCOMMENT | CM_AIN_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(IN_SuppressLevelAlarms) | 45
RCOMMENT | CM_AIN_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 46
RCOMMENT | CM_AIN_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 47
RCOMMENT | CM_AIN_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 48
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 1
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 2
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 5
RCOMMENT | CM_AOD_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_AOD_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 6
RCOMMENT | CM_AOD_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 11
RCOMMENT | CM_AOD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 18
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 19
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 20
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_AOD_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_AOD_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 24
RCOMMENT | CM_AOD_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 25
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 28
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 29
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 32
RCOMMENT | CM_AOD_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 33
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 41
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUN | MOV(3,UDT.VAL.HMIState) | 43
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL OFF | MOV(4,UDT.VAL.HMIState) | 44
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUN | MOV(5,UDT.VAL.HMIState) | 45
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO OFF | MOV(6,UDT.VAL.HMIState) | 46
RCOMMENT | CM_AOD_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 49
RCOMMENT | CM_AOD_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 50
RCOMMENT | CM_AOD_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 51
RCOMMENT | CM_AOD_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 52
RCOMMENT | CM_AOD_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 53
RCOMMENT | CM_AOD_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 54
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.SET.ManSetpoint,UDT.VAL.CVScaled) | 1
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | MESSAGES: Analog Output | MOV(UDT.OUT.CV,OUT_CV) | 2
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 3
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 4
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 5
RCOMMENT | CM_AOUT_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_AOUT_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_AOUT_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(Disabled) | 9
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 17
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 18
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 19
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 20
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_AOUT_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_AOUT_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.Opened) | 24
RCOMMENT | CM_AOUT_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.Closed) | 25
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 26
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 28
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 30
RCOMMENT | CM_AOUT_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 31
RCOMMENT | CM_AOUT_V3:AOI | Logic | VALUE: CV Calculation | MOV(100,UDT.SET.ManSetpoint) | 35
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR COMMANDS | MOV(UDT.OUT.CV,OUT_CV) | 36
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 42
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 2 FAULT ACKNOWLEDGE | MOV(2,UDT.VAL.HMIState) | 43
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 44
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 45
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 46
RCOMMENT | CM_AOUT_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 47
RCOMMENT | CM_AOUT_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 48
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 49
RCOMMENT | CM_AOUT_V3:AOI | Logic | MESSAGES: Analog Output | MOV(UDT.OUT.CV,OUT_CV) | 51
RCOMMENT | CM_AOUT_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 53
RCOMMENT | CM_AOUT_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 54
RCOMMENT | CM_AOUT_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 55
RCOMMENT | CM_AOUT_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 56
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 1
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_DIFF_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_DIFF_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DIFF_V3:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 2
RCOMMENT | CM_DIFF_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.LoTimer.PRE,1000,UDT.CFG.LoFaultTime) | 6
RCOMMENT | CM_DIFF_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 7
RCOMMENT | CM_DIFF_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 8
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 15
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 16
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 17
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 18
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.FLT.HiHi) | 19
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.HiHi) | 20
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 21
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.FLT.LoLo) | 22
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 23
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Primary Device Is Faulted of Not Enabled$N | OTL(UDT.FLT.HighRefDevice) | 24
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Secondary Device Is Faulted of Not Enabled$N | OTL(UDT.FLT.LowRefDevice) | 25
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 27
RCOMMENT | CM_DIFF_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 28
RCOMMENT | CM_DIFF_V3:AOI | Logic | Move & Calculate Values$N | SUB(UDT.VAL.HighRefActual,UDT.VAL.LowRefActual,UDT.VAL.Differential) | 31
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 36
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 37
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 5 NORMAL CONDITIONS | MOV(5,UDT.VAL.HMIState) | 38
RCOMMENT | CM_DIFF_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 39
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 40
RCOMMENT | CM_DIFF_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.DisableAlarms) | 41
RCOMMENT | CM_DIFF_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 42
RCOMMENT | CM_DIFF_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DIFF_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Unlatch) | 1
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_DI_V5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | CM_DI_V5:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DI_V5:AOI | Logic | TIMER PRESETS | MOV(1000000,UDT.WRK.Cycle_Counter.PRE) | 8
RCOMMENT | CM_DI_V5:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 9
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 16
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 17
RCOMMENT | CM_DI_V5:AOI | Logic | Delay Timer: Signal Delay Timer | RES(UDT.WRK.Delay_ON) | 19
RCOMMENT | CM_DI_V5:AOI | Logic | STATUS: Actual Digital Status | OTE(UDT.STS.Actual) | 23
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 24
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 25
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Reset Faults$N | OTU(ZoneLink.FaultExists) | 26
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.InputCard) | 27
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 28
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Input Is Fault$N | OTL(UDT.FLT.InputIsFault) | 29
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Generate Fault Code$N | OTL(UDT.STS.Faulted) | 35
RCOMMENT | CM_DI_V5:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 36
RCOMMENT | CM_DI_V5:AOI | Logic | STATUS: Simulation Mode Status | OTE(STS_SIM) | 40
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: Faulted$N | MOV(1,UDT.VAL.HMIState) | 41
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: Warning$N | MOV(2,UDT.VAL.HMIState) | 42
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 5 INPUT ON | MOV(5,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 6 INPUT OFF | MOV(6,UDT.VAL.HMIState) | 44
RCOMMENT | CM_DI_V5:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 45
RCOMMENT | CM_DI_V5:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.FLT.FaultCode) | 46
RCOMMENT | CM_DI_V5:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Unlatch) | 47
RCOMMENT | CM_DI_V5:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 48
RCOMMENT | CM_DI_V5:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 49
RCOMMENT | CM_DI_V5:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 50
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DOUT_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_DOUT_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 6
RCOMMENT | CM_DOUT_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 11
RCOMMENT | CM_DOUT_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(UDT.WRK.InUseResltCntrl) | 18
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 19
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 20
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 21
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 22
RCOMMENT | CM_DOUT_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 23
RCOMMENT | CM_DOUT_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.ON) | 24
RCOMMENT | CM_DOUT_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.OFF) | 25
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 28
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 29
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 34
RCOMMENT | CM_DOUT_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 35
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 43
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 44
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUN | MOV(3,UDT.VAL.HMIState) | 45
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL OFF | MOV(4,UDT.VAL.HMIState) | 46
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUN | MOV(5,UDT.VAL.HMIState) | 47
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO OFF | MOV(6,UDT.VAL.HMIState) | 48
RCOMMENT | CM_DOUT_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 51
RCOMMENT | CM_DOUT_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.Man) | 52
RCOMMENT | CM_DOUT_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 53
RCOMMENT | CM_DOUT_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 54
RCOMMENT | CM_DOUT_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Output) | 55
RCOMMENT | CM_DOUT_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 56
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Running Status | TOF(UDT.WRK.tmrRunning,0,0) | 5
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | MOV(IN_Cycle_CountB,UDT.IN.Cycle_CountB) | 6
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS$N | MOV(0.0,UDT.IN.Pressure_Indicator) | 7
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth_Cycle) | 8
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTU(UDT.IN.InputHealth_Pressure) | 9
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.OutputCardHealth) | 10
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 13
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 14
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | TIMER PRESETS | DIV(tmrPairStartDelay.PRE,1000,UDT.CFG.PairStopDelay) | 17
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CPT(UDT.VAL.ScaledPressure,UDT.CFG.EngPressureLow+((UDT.IN.Pressure_Indicator-UDT.CFG.RawPressureLow)/(UDT.CFG.RawPressureHigh-UDT.CFG.RawPressureLow)*(UDT.CFG.EngPressureHigh-UDT.CFG.EngPressureLow))) | 25
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CLR(UDT.VAL.ScaledPressure) | 26
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | Input: Mass Flow Rate | MOV(UDT.WRK.tmrFlowRateAcc.ACC,UDT.WRK.nFlowRatePreviousTime) | 27
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CALCULATE DELTA | CLR(UDT.WRK.CurrentSampleCycles) | 28
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | VALUE: Analog Input | CLR(UDT.VAL.CyclesPerMinB) | 29
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.Interlock) | 34
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 35
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bWorkingRunCmd) | 36
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 38
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OutputCard) | 39
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.CyclesEmptyThreshold) | 42
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.Empty) | 43
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.bWorkingFailedtoRun) | 44
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Stop Check | OTE(UDT.WRK.bWorkingFailedtoStop) | 45
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 46
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Failed to Run, Failed to Stop | OTL(UDT.FLT.FailedToStop) | 47
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 48
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Cycle Counter input Card$N | OTL(UDT.FLT.InputCard_Cycle) | 49
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Pressure Indicator input Card$N | OTL(UDT.FLT.InputCard_Pressure) | 50
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Pump Solenoid Output Card$N | OTL(UDT.FLT.OutputCard) | 51
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDInMan) | 52
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Fault Code Generation | OTU(UDT.WRK.bWorkingRunCmd) | 56
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 57
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 62
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | CLEAR COMMANDS | OTU(UDT.CMD.RunTimeReset) | 69
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 1 Faulted | MOV(1,UDT.VAL.HMIState) | 71
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 2 Warning | MOV(2,UDT.VAL.HMIState) | 72
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 73
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 74
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 75
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 76
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | HMI Device Status: STATE 0 DISABLED | MOV(0,UDT.VAL.HMIState) | 77
RCOMMENT | CM_DPHPAIR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 79
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Control.LogicDefinedPt00Data) | 3
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_E3001S_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_HI4050_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_HI4050_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_HI4050_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_HI4050_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_HI4050_V3:AOI | Logic | Sequence for reading a floating point from Scale transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 5
RCOMMENT | CM_HI4050_V3:AOI | Logic | A/D Conversion Error or A/D Failure$N | OTL(UDT.FLT.Custom.0) | 12
RCOMMENT | CM_HI4050_V3:AOI | Logic | Center Of Zero | OTL(UDT.FLT.Custom.1) | 13
RCOMMENT | CM_HI4050_V3:AOI | Logic | Weight Overrange$N | OTL(UDT.FLT.Custom.2) | 14
RCOMMENT | CM_HI4050_V3:AOI | Logic | Real Time Clock Failure$N | OTL(UDT.FLT.Custom.3) | 15
RCOMMENT | CM_HI4050_V3:AOI | Logic | SD Card Read/Write Error$N | OTL(UDT.FLT.Custom.4) | 16
RCOMMENT | CM_HI4050_V3:AOI | Logic | Motion Error$N | OTL(UDT.FLT.Custom.5) | 17
RCOMMENT | CM_HI4050_V3:AOI | Logic | Display Error$N | OTL(UDT.FLT.Custom.6) | 18
RCOMMENT | CM_HI4050_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 22
RCOMMENT | CM_HI4050_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 23
RCOMMENT | CM_HI4050_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 24
RCOMMENT | CM_HI4050_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 25
RCOMMENT | CM_HI4050_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 26
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_HI6500_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_HI6500_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_HI6500_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_HI6500_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_HI6500_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 12
RCOMMENT | CM_HI6500_V3:AOI | Logic | A/D Conversion Error or A/D Failure$N | OTL(UDT.FLT.Custom.0) | 14
RCOMMENT | CM_HI6500_V3:AOI | Logic | Center Of Zero | OTU(UDT.FLT.Custom.1) | 15
RCOMMENT | CM_HI6500_V3:AOI | Logic | Weight Overrange$N | OTU(UDT.FLT.Custom.2) | 16
RCOMMENT | CM_HI6500_V3:AOI | Logic | Real Time Clock Failure$N | OTU(UDT.FLT.Custom.3) | 17
RCOMMENT | CM_HI6500_V3:AOI | Logic | SD Card Read/Write Error$N | OTL(UDT.FLT.Custom.4) | 18
RCOMMENT | CM_HI6500_V3:AOI | Logic | Motion Error$N | OTU(UDT.FLT.Custom.5) | 19
RCOMMENT | CM_HI6500_V3:AOI | Logic | Display Error$N | OTU(UDT.FLT.Custom.6) | 20
RCOMMENT | CM_HI6500_V3:AOI | Logic | Test In Progress | OTL(UDT.FLT.Custom.7) | 21
RCOMMENT | CM_HI6500_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 27
RCOMMENT | CM_HI6500_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 28
RCOMMENT | CM_HI6500_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 29
RCOMMENT | CM_HI6500_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 30
RCOMMENT | CM_HI6500_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_IND560E_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_IND560E_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_IND560E_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_IND560E_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_IND560E_V3:AOI | Logic | Sequence for reading a floating point from IND560 transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 9
RCOMMENT | CM_IND560E_V3:AOI | Logic | Update the Command to the IND570$N$NThe IND570 only acts on a command if it sees a change from the previous command. That means if you need to send another Tare after the first Tare, there must be another command between them - such as Display Net Weight.$N$NThis rung waits until the comand changes, then it writes the Command, and the Command Data to the PLC$'s output buffer to the IND570. It then updates the history.$N$NNote that the MOV command that moves Command_Data to Command_Data is used to display or modify the value easily. This move can be deleted from your program.$N$N | MOV(Command,CommandPrev) | 16
RCOMMENT | CM_IND560E_V3:AOI | Logic | Various example commands$N$N$NThis rung allows triggering of some sample commands to the IND570. Your own logic does not need to function this way. It only needs to write a value to $QCommand$Q, and if necessary, to $QCommand_Data.$Q $N$NThe MOV instruction for FloatingPoint_Data is only so that the returned data is easy to read after one of the command bits has been set.$N$NOther commands that can be sent to the IND570 can be found in $Nthe PLC Interface Manual.$N$N | MOV(11,Command) | 17
RCOMMENT | CM_IND560E_V3:AOI | Logic | $NMap the Floating Point Input Indicator bits into a word so we can decode what type of data the IND570 is currently returning to us. See in the PLC Inteface Manual for a mapping of these values.$N$N | MOV(-1,DataReturned) | 18
RCOMMENT | CM_IND560E_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 19
RCOMMENT | CM_IND560E_V3:AOI | Logic | Scale Controller Is Powering-Up or In Config Mode | OTL(UDT.FLT.Custom.1) | 22
RCOMMENT | CM_IND560E_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 27
RCOMMENT | CM_IND560E_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 28
RCOMMENT | CM_IND560E_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 29
RCOMMENT | CM_IND560E_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 30
RCOMMENT | CM_IND560E_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_IND570E_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_IND570E_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_IND570E_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_IND570E_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_IND570E_V3:AOI | Logic | Sequence for reading a floating point from IND560 transitter :$NWords 1 and 2 from the transmitter comprise the floating point value in IEEE 754 format.$NFor Control Logix to interpret the data; words 1 and 2 must be swaped into an array of ints.$NThe integer array is then copied into a floating point tag. | MOV(UDT.SET.SIM,UDT.VAL.ActualWeight) | 7
RCOMMENT | CM_IND570E_V3:AOI | Logic | Update the Command to the IND570$N$NThe IND570 only acts on a command if it sees a change from the previous command. That means if you need to send another Tare after the first Tare, there must be another command between them - such as Display Net Weight.$N$NThis rung waits until the comand changes, then it writes the Command, and the Command Data to the PLC$'s output buffer to the IND570. It then updates the history.$N$NNote that the MOV command that moves Command_Data to Command_Data is used to display or modify the value easily. This move can be deleted from your program.$N$N | MOV(Command,CommandPrev) | 14
RCOMMENT | CM_IND570E_V3:AOI | Logic | Various example commands$N$N$NThis rung allows triggering of some sample commands to the IND570. Your own logic does not need to function this way. It only needs to write a value to $QCommand$Q, and if necessary, to $QCommand_Data.$Q $N$NThe MOV instruction for FloatingPoint_Data is only so that the returned data is easy to read after one of the command bits has been set.$N$NOther commands that can be sent to the IND570 can be found in $Nthe PLC Interface Manual.$N$N | MOV(11,Command) | 15
RCOMMENT | CM_IND570E_V3:AOI | Logic | $NMap the Floating Point Input Indicator bits into a word so we can decode what type of data the IND570 is currently returning to us. See in the PLC Inteface Manual for a mapping of these values.$N$N | MOV(-1,DataReturned) | 16
RCOMMENT | CM_IND570E_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 17
RCOMMENT | CM_IND570E_V3:AOI | Logic | Scale Controller Is Powering-Up or In Config Mode | OTL(UDT.FLT.Custom.1) | 20
RCOMMENT | CM_IND570E_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 25
RCOMMENT | CM_IND570E_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 26
RCOMMENT | CM_IND570E_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 27
RCOMMENT | CM_IND570E_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 28
RCOMMENT | CM_IND570E_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 29
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2_NoControl:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_2_OL:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_4:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_4_MOR:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_HI) | 3
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Run) | 3
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_GS_5:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.FLT.FaultCode,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Stop) | 3
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_RCH_6:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoReverse) | 0
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 1
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 3
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_RCH_7:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 0
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoStop) | 1
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 3
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_M2S_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 9
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 10
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 11
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(5000,UDT.WRK.tmrIllegalHOA.PRE) | 33
RCOMMENT | CM_M2S_V3:AOI | Logic | VAL.InUseBy is a DINT array that contains Integers values of the $'owners$' of this CM$N$N | RES(UDT.WRK.InUseResltCntrl) | 40
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Pre-Processing Stop PB In Auto Running | OTE(UDT.WRK.StopPBWhileRunAuto) | 41
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Hand Operation Start & Stop$N | OTU(UDT.WRK.bInternalRun) | 42
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.WRK.bInternalRun) | 43
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Manual Run/Stop | OTU(UDT.WRK.bInternalRun) | 44
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Hand Operation Start & Stop$N | OTU(UDT.WRK.bInternalRun) | 45
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop Transition Through Slow$N | OTL(UDT.STS.StopTransitioning) | 46
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER: Stop Transitioning Maintain Timer | OTU(UDT.STS.StopTransitioning) | 47
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Single Speed Run$N | OTU(UDT.STS.Fast) | 48
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Fast-Slow Speed Motor Command Processing$N | OTL(UDT.STS.Fast) | 49
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Forward-Reverse Motor Command Processing$N | OTL(UDT.STS.Reverse) | 50
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop / OFF Command Processing$N | OTU(UDT.WRK.bInternalRun) | 51
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 52
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 53
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.RunTimeFault) | 54
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Overload | OTE(UDT.STS.Overload) | 55
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Disconnect | OTE(UDT.STS.Disconnect) | 56
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Running Status | OTE(UDT.STS.Running) | 57
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Stopped Status | OTE(UDT.STS.Stopped) | 60
RCOMMENT | CM_M2S_V3:AOI | Logic | STATUS: Ramp (Stopping) Status | OTE(UDT.STS.Stopping) | 61
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.FailingToStart) | 65
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Stop Check | OTE(UDT.WRK.FailingToStop) | 66
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run Check | OTE(UDT.WRK.FailingToStartTransition) | 67
RCOMMENT | CM_M2S_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrMotorTransition,5000,0) | 68
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Failed to Run, Failed to Stop | OTU(ExternalFault) | 69
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Overload) | 70
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Stop PB Pressed While Running In Auto | OTL(UDT.FLT.StopPBInAuto) | 71
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 72
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 73
RCOMMENT | CM_M2S_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 82
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Stop Transition Through Slow After Fault | OTL(UDT.STS.StopTransitioning) | 86
RCOMMENT | CM_M2S_V3:AOI | Logic | COMMAND: Start Transition Through Slow$N | OTL(UDT.STS.StartTransitioning) | 87
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 1$NFAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 95
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 96
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 3$NMANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 97
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 4$NMANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 98
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 5$NAUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 99
RCOMMENT | CM_M2S_V3:AOI | Logic | HMI Device Status: STATE 6$NAUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 100
RCOMMENT | CM_M2S_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 101
RCOMMENT | CM_M2S_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 104
RCOMMENT | CM_M2S_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.AutoStart) | 105
RCOMMENT | CM_M2S_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 106
RCOMMENT | CM_M2S_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_FastOrRev) | 107
RCOMMENT | CM_M2S_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 108
RCOMMENT | CM_M2S_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 109
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METDG_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METDG_V3:AOI | Logic | CM Type ID$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METDG_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METDG_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METDG_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METDG_V3:AOI | Logic | Fault: Message to pull fault word from the meter. | MSG(MSG_Alarms) | 11
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 12
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: NVError | OTL(UDT.FLT.Custom.0) | 14
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: RAM Error | OTL(UDT.FLT.Custom.1) | 15
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: RTI Failure | OTL(UDT.FLT.Custom.2) | 16
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Sensor Failure | OTL(UDT.FLT.Custom.3) | 17
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Temperature Range | OTL(UDT.FLT.Custom.4) | 18
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Other Failure | OTL(UDT.FLT.Custom.5) | 19
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Trans Intializing | OTL(UDT.FLT.Custom.6) | 20
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Meter SIM Is ON | OTL(UDT.FLT.Custom.7) | 21
RCOMMENT | CM_METDG_V3:AOI | Logic | FAULT: Watchdog Error$N | OTL(UDT.FLT.Custom.8) | 22
RCOMMENT | CM_METDG_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 26
RCOMMENT | CM_METDG_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_VolTotal,UDT.INOUT.VolumeTotal) | 28
RCOMMENT | CM_METDG_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 29
RCOMMENT | CM_METDG_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 30
RCOMMENT | CM_METDG_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 31
RCOMMENT | CM_METDG_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 32
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoEnable[0],CMDSize) | 1
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METP4_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METP4_V3:AOI | Logic | Program Name: Totalize_Freq$NRoutine Name: Totalize_Freq$NDescription: Totalizer Device Control Module$NVariation: For Use With Pulse Module (IP4) | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METP4_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METP4_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METP4_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METP4_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | ADD(UDT.INOUT.RolloverCountVol,1,UDT.INOUT.RolloverCountVol) | 13
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_MassTotal,(UDT.INOUT.RolloverCountMass*UDT.CFG.RollOverMass)+UDT.INOUT.MassTotal) | 14
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.MassTotal,localPrevMassTotal) | 15
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_VolTotal,(UDT.INOUT.RolloverCountVol*UDT.CFG.RollOverVolume) + UDT.INOUT.VolumeTotal) | 16
RCOMMENT | CM_METP4_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 17
RCOMMENT | CM_METP4_V3:AOI | Logic | FAULT: Control Module Fault | OTE(STS_InUse) | 19
RCOMMENT | CM_METP4_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 23
RCOMMENT | CM_METP4_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 25
RCOMMENT | CM_METP4_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 26
RCOMMENT | CM_METP4_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 27
RCOMMENT | CM_METP4_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 28
RCOMMENT | CM_METP4_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 29
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METPAIR_V3:AOI | Logic | Find the UserID of the Currently Connected User | RES(InUseResltCntrl) | 10
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_METPG_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_METPG_V3:AOI | Logic | Program Name: MPG$NDescription: Totalizer Device Control Module$NVariation: For Use With Pulse Module (IP4) | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_METPG_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_METPG_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_METPG_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_METPG_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | ADD(UDT.INOUT.RolloverCountVol,1,UDT.INOUT.RolloverCountVol) | 15
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_MassTotal,(UDT.INOUT.RolloverCountMass*UDT.CFG.RollOverMass)+UDT.INOUT.MassTotal) | 16
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.MassTotal,localPrevMassTotal) | 17
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | CPT(CM_MET.IN_VolTotal,(UDT.INOUT.RolloverCountVol*UDT.CFG.RollOverVolume) + UDT.INOUT.VolumeTotal) | 18
RCOMMENT | CM_METPG_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.INOUT.VolumeTotal,localPrevVolumeTotal) | 19
RCOMMENT | CM_METPG_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 21
RCOMMENT | CM_METPG_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_RawVolume,UDT.INOUT.VolumeTotal) | 23
RCOMMENT | CM_METPG_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 24
RCOMMENT | CM_METPG_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 25
RCOMMENT | CM_METPG_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 26
RCOMMENT | CM_METPG_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 27
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Density | MOV(UDT.IN.Density,UDT.VAL.Density) | 1
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Total | ADD(UDT.IN.VolumeTotal,UDT.SET.SIMDeltaPerScanVolume,UDT.IN.VolumeTotal) | 2
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow | MOV(UDT.IN.MassFlow,UDT.VAL.MassFlowRate) | 3
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow | MOV(UDT.IN.VolumeFlow,UDT.VAL.VolumeFlowRate) | 4
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Temperature | MOV(UDT.IN.Temp,UDT.VAL.Temp) | 5
RCOMMENT | CM_MET_V3:AOI | Logic | Value: DriveGain | COP(IN_DriveGain,UDT.VAL.DriveGain,1) | 6
RCOMMENT | CM_MET_V3:AOI | Logic | INPUT: Zone Link Interlock Status$N | OTE(UDT.IN.Interlock) | 8
RCOMMENT | CM_MET_V3:AOI | Logic | INPUT: ZoneLink ID #$N | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 9
RCOMMENT | CM_MET_V3:AOI | Logic | Value: Calculated Volumeteric Flow Rate | MOV(0,UDT.VAL.VolumeFlowRate) | 10
RCOMMENT | CM_MET_V3:AOI | Logic | TIMER PRESETS | MOV(1000000,tmrVolumeFlowRateAcc.PRE) | 11
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | RES(InUseResltCntrl) | 17
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | RES(tmrLowDensity) | 20
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | RES(tmrLowDensity) | 21
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 22
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 23
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto/Manual Zero | MOV(UDT.SET.Preact,UDT.VAL.Preact) | 24
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Auto/Manual Zero | DIV(UDT.INOUT.MassTotal,UDT.VAL.Density,UDT.IN.VolumeTotal) | 25
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Settle | OTL(UDT.STS.SettleComplete) | 26
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS: Totalizer Complete$NACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 28
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Stop | OTL(UDT.STS.Stopping) | 29
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Stabilize | OTU(UDT.STS.SettleComplete) | 30
RCOMMENT | CM_MET_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.HiDensity) | 31
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: HI/LO Fault Timer | TON(tmrLowFlow,?,?) | 32
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoFlow) | 33
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Denisty Low Fault Timer | TON(tmrLowDensity,?,?) | 34
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoDensity) | 35
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Denisty Hi Fault Timer | TON(tmrHiDensity,?,?) | 36
RCOMMENT | CM_MET_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.HiDensity) | 37
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 38
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Auto Command While In Manual$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 39
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Stopping) | 46
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 47
RCOMMENT | CM_MET_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 50
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.MassFlowRate) | 51
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.IN.MassTotal,rTotalPreviousScan_Mass) | 52
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | CLR(rTotalSinceInit_Mass) | 53
RCOMMENT | CM_MET_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.VolumeFlowRate) | 54
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.IN.VolumeTotal,rTotalPreviousScan_VOL) | 55
RCOMMENT | CM_MET_V3:AOI | Logic | CALCULATE DELTA | CLR(rTotalSinceInit_VOL) | 56
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.MassTotal,UDT.VAL.AmountRemain) | 57
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.VolumeTotal,UDT.VAL.AmountRemain) | 58
RCOMMENT | CM_MET_V3:AOI | Logic | VALUE: Temperature | MOV(UDT.IN.Temp,UDT.VAL.Temp) | 59
RCOMMENT | CM_MET_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.STS.InUse) | 60
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 1 | MOV(1,UDT.VAL.HMIState) | 65
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 1 | MOV(2,UDT.VAL.HMIState) | 66
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 3 | MOV(3,UDT.VAL.HMIState) | 67
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 68
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 5 | MOV(5,UDT.VAL.HMIState) | 69
RCOMMENT | CM_MET_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 70
RCOMMENT | CM_MET_V3:AOI | Prescan | CALCULATE DELTA | OTL(UDT.STS.Stopping) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 1
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_MM5700IP_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | CM Type ID$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 5
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 13
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: NVError | OTL(UDT.FLT.Custom.0) | 15
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: RAM Error | OTL(UDT.FLT.Custom.1) | 16
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: RTI Failure | OTL(UDT.FLT.Custom.2) | 17
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Sensor Failure | OTL(UDT.FLT.Custom.3) | 18
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Temperature Range | OTL(UDT.FLT.Custom.4) | 19
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Other Failure | OTL(UDT.FLT.Custom.5) | 20
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Trans Intializing | OTL(UDT.FLT.Custom.6) | 21
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Meter SIM Is ON | OTL(UDT.FLT.Custom.7) | 22
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Watchdog Error$N | OTL(UDT.FLT.Custom.8) | 23
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Comm Loss$N | OTL(UDT.FLT.Custom.9) | 24
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Tube Not Full or Drive Overrange$N | OTL(UDT.FLT.Custom.10) | 25
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | FAULT: Mass Flow Overrange OR Density Overrange | OTL(UDT.FLT.Custom.11) | 26
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 29
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(IN_Status.Totalizer_2,UDT.INOUT.VolumeTotal) | 31
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],CMDSize) | 34
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 35
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 36
RCOMMENT | CM_MM5700IP_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 37
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_ControlValue) | 4
RCOMMENT | CM_PID_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 4
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrLoopOscillating.PRE,1000,UDT.CFG.OscillationDelayTime) | 8
RCOMMENT | CM_PID_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | MOV(UDT.CFG.EngMax,PIDLoop.MAXTIE) | 12
RCOMMENT | CM_PID_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 13
RCOMMENT | CM_PID_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 14
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 15
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(IN_Setpoint,PIDLoop.SP) | 16
RCOMMENT | CM_PID_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 17
RCOMMENT | CM_PID_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 18
RCOMMENT | CM_PID_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 19
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 20
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 21
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 22
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 23
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 24
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 25
RCOMMENT | CM_PID_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 26
RCOMMENT | CM_PID_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrFaultDelay.PRE,1000,UDT.CFG.FaultDelayTime) | 30
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 37
RCOMMENT | CM_PID_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 40
RCOMMENT | CM_PID_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 41
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 42
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 43
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 44
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | CM_PID_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.OscillationDeviation) | 46
RCOMMENT | CM_PID_V3:AOI | Logic | VALUE Deviation Limit Values | SUB(PIDLoop.SP,UDT.CFG.AlarmDeviation,UDT.VAL.LoLoDeviation) | 47
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Loop in Control | OTL(UDT.STS.InControl) | 48
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Loop Out of Control | OTU(UDT.STS.InControl) | 49
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Oscillation of PV | OTE(UDT.STS.Oscillating) | 50
RCOMMENT | CM_PID_V3:AOI | Logic | STATUS Hi Hi, Hi, Lo, Lo Lo Deviation Status | OTE(UDT.STS.LoLoDeviation) | 51
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HIHI/LOLO Deviation Fault Timer | TON(UDT.WRK.tmrWarningDelay,0,499) | 52
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HI/LO Fault Timer | TON(UDT.WRK.tmrAlarmDelay,0,0) | 53
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HIHI Deviation | OTL(UDT.FLT.HiHiDeviation) | 54
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT HI Deviation | OTE(UDT.FLT.HiDeviation) | 55
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Lo Deviation | OTE(UDT.FLT.LoDeviation) | 56
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Lo Lo Deviation | OTL(UDT.FLT.LoLoDeviation) | 57
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT Oscillation in PV | OTL(UDT.FLT.OscillationDeviation) | 58
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 59
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 60
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.WRK.bWorkingOpenValve) | 62
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 63
RCOMMENT | CM_PID_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 67
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 73
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 74
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 75
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 76
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 77
RCOMMENT | CM_PID_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 78
RCOMMENT | CM_PID_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 79
RCOMMENT | CM_PID_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 81
RCOMMENT | CM_PID_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 82
RCOMMENT | CM_PID_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 83
RCOMMENT | CM_PID_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 84
RCOMMENT | CM_PID_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(UDT.OUT.CV,OUT_ControlValue) | 85
RCOMMENT | CM_PID_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_ControlValue) | 86
RCOMMENT | CM_PID_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 87
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 1
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],UDT.WRK.CMDAutoZeroSize) | 2
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.OutputDisable) | 3
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_PMR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_PMR_V3:AOI | Logic | Grundfos Metering Pump Estimated Delivery$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto/Manual$NSTATUS: Mode | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: ZoneLink Simulation Status$N | OTE(UDT.IN.SIM) | 4
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Zone Link Interlock Status$N | OTE(UDT.IN.Interlock) | 9
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Input Channel Health | OTE(UDT.IN.InHealth_PanelEstop) | 10
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Input Channel Health | OTE(UDT.IN.InHealth_PumpFault) | 11
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: Output Channel Health | OTE(UDT.IN.OutputHealth) | 12
RCOMMENT | CM_PMR_V3:AOI | Logic | INPUT: ZoneLink ID #$N | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 13
RCOMMENT | CM_PMR_V3:AOI | Logic | TIMER PRESETS | MOV(3600000,UDT.WRK.tmrRunTime.PRE) | 14
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 21
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | OTU(UDT.STS.Complete) | 24
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto Start/Stop Accumulating Quantity$NSTATUS: Totalizer Accumulating Quantity (RUN) | OTU(UDT.STS.Complete) | 25
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 26
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 27
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Auto/Manual Zero | RES(UDT.WRK.tmrTimedDelivery) | 28
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Stop | OTU(UDT.STS.Running) | 29
RCOMMENT | CM_PMR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 30
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 31
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.InputCard) | 32
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Input Card Health$N | OTL(UDT.FLT.OutputCard) | 33
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Auto Command While In Manual$N | OTL(UDT.FLT.AutoCMDWhileInMan) | 34
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Pump Is Faulted$N | OTL(UDT.FLT.PumpFaulted) | 35
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 37
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 38
RCOMMENT | CM_PMR_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 41
RCOMMENT | CM_PMR_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.WRK.tmrElapsedAcc.ACC,UDT.WRK.nElapsedAccPrevious) | 42
RCOMMENT | CM_PMR_V3:AOI | Logic | STATUS: Totalizer Complete$NACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 44
RCOMMENT | CM_PMR_V3:AOI | Logic | Input: Mass Flow Rate | MOV(0,UDT.VAL.MassFlowRate) | 45
RCOMMENT | CM_PMR_V3:AOI | Logic | VALUE: Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.MassTotal,UDT.VAL.AmountRemain) | 46
RCOMMENT | CM_PMR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(STS_InUse) | 47
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(1,UDT.VAL.HMIState) | 51
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 52
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 3 | MOV(3,UDT.VAL.HMIState) | 53
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 54
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 5 | MOV(5,UDT.VAL.HMIState) | 55
RCOMMENT | CM_PMR_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 56
RCOMMENT | CM_PMR_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 57
RCOMMENT | CM_PMR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.InUseResltCntrl.LEN) | 59
RCOMMENT | CM_PMR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoZero[0],UDT.WRK.CMDAutoZeroSize) | 60
RCOMMENT | CM_PMR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.OutputDisable) | 61
RCOMMENT | CM_PMR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 62
RCOMMENT | CM_PMR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 63
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | CM_SF_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 4
RCOMMENT | CM_SF_V3:AOI | Logic | TIMER PRESETS | OTL(UDT.CFG.IsFault) | 0
RCOMMENT | CM_SF_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 2
RCOMMENT | CM_SF_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.Delay_OFF.PRE,1000,UDT.WRK.DelayAckActive.PRE) | 10
RCOMMENT | CM_SF_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 11
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 13
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT: Reset Faults$N | RES(UDT.WRK.DelayAckActive) | 14
RCOMMENT | CM_SF_V3:AOI | Logic | Delay Timer: Signal Delay Timer | TON(UDT.WRK.Delay_OFF,?,?) | 15
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Actual Digital Status | OTE(UDT.STS.Actual) | 19
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Actual Digital Status | OTL(UDT.FLT.SystemFault) | 21
RCOMMENT | CM_SF_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 24
RCOMMENT | CM_SF_V3:AOI | Logic | STATUS: Simulation Mode Status | OTE(STS_SIM) | 28
RCOMMENT | CM_SF_V3:AOI | Logic | HMI Device Status: Faulted$N | MOV(1,UDT.VAL.HMIState) | 29
RCOMMENT | CM_SF_V3:AOI | Logic | HMI Device Status: STATE 5 INPUT ON | MOV(5,UDT.VAL.HMIState) | 30
RCOMMENT | CM_SF_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 31
RCOMMENT | CM_SF_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 32
RCOMMENT | CM_SF_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 33
RCOMMENT | CM_SF_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 34
RCOMMENT | CM_SF_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 35
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_SZONE_V3:AOI | EnableInFalse | ENABLE IN FALSE: Disable Interlock Output$N | MOV(0,UDT.VAL.HMIState) | 0
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Interlock Input$N | OTE(UDT.IN.Interlock) | 2
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Interlock Input Health$N | OTE(UDT.IN.InterlockHealth) | 3
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Reverse Operation Interlock$N | OTE(UDT.IN.RevInterlock) | 4
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Push-Button | OTE(UDT.IN.SafetyRelayResetPB) | 6
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Push-Button Input Health | OTE(UDT.IN.SafetyRelayResetPBHealth) | 7
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: E-Stop Relay Reset Output Health | OTE(UDT.IN.SafetyRelayResetHealth) | 8
RCOMMENT | CM_SZONE_V3:AOI | Logic | CONNECTIONS: Zone ID$N | MOV(ZoneID,UDT.VAL.ZoneID) | 9
RCOMMENT | CM_SZONE_V3:AOI | Logic | TIMER PRESETS$N | DIV(UDT.WRK.tmrSafetyRelayReset.PRE,1000,UDT.CFG.SafetyRelayResetTime) | 10
RCOMMENT | CM_SZONE_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 11
RCOMMENT | CM_SZONE_V3:AOI | Logic | WORK: Evaluate Simulation State$N | OTU(UDT.LNK.SIM) | 12
RCOMMENT | CM_SZONE_V3:AOI | Logic | ZONE LINK: Fault Reset Holding Actions$N | OTE(UDT.LNK.FaultReset) | 16
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Safety Interlock Is OK$N | OTE(STS_InterlockOK) | 18
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Fault Code Generator$N | OTL(UDT.STS.Faulted) | 21
RCOMMENT | CM_SZONE_V3:AOI | Logic | FAULT: Clear Fault Code Register If No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 22
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WHR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WHR_V3:AOI | Logic | Redundent Valve AOI Will Not Operatate As $QDouble Acting$Q, The design does not include provisions to treat a redundent valve as double acting which would require four solenoids. | OTU(UDT.CFG.DoubleSolenoid) | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WH_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WH_V3:AOI | Logic | Auto Config Switch On First Scan$N(Pre Scan Equivalent)$N | OTU(UDT.CFG.AutoHOAInService) | 2
RCOMMENT | CM_V2WH_V3:AOI | Logic | Move AOI Inputs To Correct Registers$N | OTE(UDT.IN.HandHOA) | 3
RCOMMENT | CM_V2WH_V3:AOI | Logic | Set Current HOA Mode$N | OTE(UDT.STS.HandHOAMode) | 4
RCOMMENT | CM_V2WH_V3:AOI | Logic | Set Auto Command In Manual Fault To Warning and Clear When Not Active$N | OTU(UDT.FLT.AutoCMDWhileInMan) | 6
RCOMMENT | CM_V2WH_V3:AOI | Logic | Issue Appropriate Command For Valve Configuration$N | OTU(UDT.CMD.ManualClose) | 8
RCOMMENT | CM_V2WH_V3:AOI | Logic | Monitor Input Health of HOA Switch$N | OTE(CM_V2W_V3_AOI.IN_CLSHealth) | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2WR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2WR_V3:AOI | Logic | Redundent Valve AOI Will Not Operatate As $QDouble Acting$Q, The design does not include provisions to treat a redundent valve as double acting which would require four solenoids. | OTU(UDT.CFG.DoubleSolenoid) | 3
RCOMMENT | CM_V2WR_V3:AOI | Logic | FAULTS | TON(RedundentCheckCustomFaultsTMR,?,?) | 22
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_V2W_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V2W_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 11
RCOMMENT | CM_V2W_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosePos) | 12
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrCloseDelay.PRE,1000,UDT.CFG.CloseDelayTime) | 16
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V2W_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V2W_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 31
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 32
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V2W_V3:AOI | Logic | COMMAND: Fault Reset | OTU(ExternalFault) | 35
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V2W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToClose,0.5,UDT.VAL.TimeToClose) | 38
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 39
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 40
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 43
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.WRK.bWorkingEngValve) | 47
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 48
RCOMMENT | CM_V2W_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 52
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V2W_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 65
RCOMMENT | CM_V2W_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 66
RCOMMENT | CM_V2W_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 68
RCOMMENT | CM_V2W_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 69
RCOMMENT | CM_V2W_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 70
RCOMMENT | CM_V2W_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 71
RCOMMENT | CM_V2W_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 72
RCOMMENT | CM_V2W_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 73
RCOMMENT | CM_V2W_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 74
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 4
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 5
RCOMMENT | CM_V3D_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V3D_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InToBPos) | 6
RCOMMENT | CM_V3D_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InToAPos) | 7
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrToADelay.PRE,1000,UDT.CFG.ToADelayTime) | 16
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V3D_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V3D_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingToBValve) | 31
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingToBValve) | 32
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V3D_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 35
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToB,0.5,UDT.VAL.TimeToB) | 38
RCOMMENT | CM_V3D_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToA,0.5,UDT.VAL.TimeToA) | 39
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingToBValve) | 46
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_V3D_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V3D_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V3D_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_V3D_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_V3D_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_V3D_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_V3D_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_V3D_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 71
RCOMMENT | CM_V3D_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 72
RCOMMENT | CM_V3D_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 4
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 5
RCOMMENT | CM_V3W_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_V3W_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InDivertPos) | 11
RCOMMENT | CM_V3W_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InStraightPos) | 12
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrStraightDelay.PRE,1000,UDT.CFG.StraightDelayTime) | 16
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 23
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_V3W_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 29
RCOMMENT | CM_V3W_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingDivertValve) | 31
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingDivertValve) | 32
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 33
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 34
RCOMMENT | CM_V3W_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 35
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 36
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 37
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToDivert,0.5,UDT.VAL.TimeToDivert) | 38
RCOMMENT | CM_V3W_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToStraight,0.5,UDT.VAL.TimeToStraight) | 39
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingDivertValve) | 46
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_V3W_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 60
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_V3W_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_V3W_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_V3W_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_V3W_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_V3W_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_V3W_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_V3W_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Out1) | 71
RCOMMENT | CM_V3W_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Out2) | 72
RCOMMENT | CM_V3W_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 6
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Close Status | OTE(UDT.STS.InClosePos) | 7
RCOMMENT | CM_VDB_V3:AOI | Logic | STATUS: Dribble Status | OTE(UDT.STS.InDribblePos) | 8
RCOMMENT | CM_VDB_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrDribbleDelay.PRE,1000,UDT.CFG.DribbleDelayTime) | 18
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 25
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 26
RCOMMENT | CM_VDB_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 31
RCOMMENT | CM_VDB_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 32
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(UDT.WRK.ReqDribble) | 34
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 35
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 36
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 37
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 38
RCOMMENT | CM_VDB_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 39
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bFeedbackLS) | 40
RCOMMENT | CM_VDB_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 41
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 42
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 43
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 46
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 47
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 48
RCOMMENT | CM_VDB_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 52
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 61
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 62
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 63
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 64
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 65
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 66
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 7 MANUAL DRIBBLE | MOV(7,UDT.VAL.HMIState) | 67
RCOMMENT | CM_VDB_V3:AOI | Logic | HMI Device Status: STATE 8 AUTO DRIBBLE | MOV(8,UDT.VAL.HMIState) | 68
RCOMMENT | CM_VDB_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 69
RCOMMENT | CM_VDB_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 71
RCOMMENT | CM_VDB_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 72
RCOMMENT | CM_VDB_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 73
RCOMMENT | CM_VDB_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 74
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Open) | 76
RCOMMENT | CM_VDB_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | OTE(OUT_Dribble) | 77
RCOMMENT | CM_VDB_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 78
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 4
RCOMMENT | CM_VFD2S_MOR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 8
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 9
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 10
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(UDT.CFG.HighSpeedSet,UDT.SET.ManualCV) | 24
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 26
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 31
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 32
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 33
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 34
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 35
RCOMMENT | CM_VFD2S_MOR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 36
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_VFD.Stop) | 4
RCOMMENT | CM_VFD525Ctrl_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 34
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 39
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 40
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 41
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 42
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | OUTPUT: Setpoint | MUL(UDT.OUT.Reference,60,OUT_VFD.FreqCommand) | 44
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 45
RCOMMENT | CM_VFD525Ctrl_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 46
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 4
RCOMMENT | CM_VFD755_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFD755_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFD755_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFD755_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFD755_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 32
RCOMMENT | CM_VFD755_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 37
RCOMMENT | CM_VFD755_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 38
RCOMMENT | CM_VFD755_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 39
RCOMMENT | CM_VFD755_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 40
RCOMMENT | CM_VFD755_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 43
RCOMMENT | CM_VFD755_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.OUT.Reference,UDT.SET.ManualCV) | 4
RCOMMENT | CM_VFDANA_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDANA_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFDANA_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 8
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 9
RCOMMENT | CM_VFDANA_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 10
RCOMMENT | CM_VFDANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 24
RCOMMENT | CM_VFDANA_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 30
RCOMMENT | CM_VFDANA_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 31
RCOMMENT | CM_VFDANA_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 32
RCOMMENT | CM_VFDANA_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(UDT.OUT.Reference,UDT.SET.ManualCV) | 36
RCOMMENT | CM_VFDANA_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 37
RCOMMENT | CM_VFDANA_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 38
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 0
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 1
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Command.6) | 3
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 5
RCOMMENT | CM_VFDCH_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CM Routine Name: CM_PF70_5_AOI$N$NDescription: PowerFlex 70 Firmware 5.1$N$N | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VFDCH_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_VFDCH_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 20
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 21
RCOMMENT | CM_VFDCH_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 22
RCOMMENT | CM_VFDCH_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 38
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 44
RCOMMENT | CM_VFDCH_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 45
RCOMMENT | CM_VFDCH_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 46
RCOMMENT | CM_VFDCH_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 47
RCOMMENT | CM_VFDCH_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 49
RCOMMENT | CM_VFDCH_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 50
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF700_V1:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF700_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF700_V2:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF700_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF70_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 10
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 11
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 12
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 31
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 36
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 37
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 38
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 39
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 42
RCOMMENT | CM_VFDPF70_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 43
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 1
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 2
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 3
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(Inhealth_Stop) | 4
RCOMMENT | CM_VFDPF753_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 4
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 5
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Auto Position Status | OTE(UDT.STS.Auto) | 11
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Hand Position Status | OTE(UDT.STS.Hand) | 12
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | STATUS: HOA Off Position Status | OTE(UDT.STS.Off) | 13
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | Sim Logic Changed From the AFI branch to the new$Nbranch. | CPT(UDT.VAL.RPM,(UDT.VAL.ActualSpeed/100) * UDT.VAL.RefMax) | 30
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 32
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 37
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ReadReference) | 38
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 39
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Enable) | 40
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_InUse) | 43
RCOMMENT | CM_VFDPF753_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 44
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VFD_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 24
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 25
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 26
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 27
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 28
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 29
RCOMMENT | CM_VFD_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 30
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 31
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 32
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(SpeedValidate,PIDLoop.SO) | 33
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | CLR(UDT.VAL.SpeedSP) | 34
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.Flowrate,PIDLoop.SP) | 35
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundDown) | 36
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 37
RCOMMENT | CM_VFD_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundDown) | 38
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS$NControl Action | OTL(PIDLoop.CA) | 39
RCOMMENT | CM_VFD_V3:AOI | Logic | InUse: Determine if CM Is In Use$N | RES(InUseResltCntrl) | 48
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND: Auto Run/Stop | OTU(UDT.INOUT.bWorkingRunCmd) | 49
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 50
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS/OUTPUT: ENABLE VFD$N | OTE(UDT.STS.VFDEnabled) | 51
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS/OUTPUT: MANUAL ENABLE$N | OTE(UDT.STS.ManualEnabled) | 52
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: START COMMAND TO VFD | OTL(UDT.INOUT.ReqRunHold) | 53
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: STOP COMMAND TO VFD | OTU(UDT.INOUT.ReqRunHold) | 54
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 58
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 59
RCOMMENT | CM_VFD_V3:AOI | Logic | COMMAND: Fault Reset | OTE(UDT.OUT.ResetFault) | 60
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Drive Fault | OTL(UDT.FLT.DriveFault) | 61
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 62
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Disconnect | OTE(UDT.STS.DisconnectActive) | 63
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Disconnect | OTL(UDT.FLT.DisconnectFault) | 64
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Input Card/Channel Faulted$N | OTL(UDT.FLT.InputCard) | 65
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Output Card/Channel Faulted$N | OTL(UDT.FLT.OutputCard) | 66
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Illegal Feedback | OTL(UDT.FLT.IllegalFeedback) | 67
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Failed To Run | OTL(UDT.FLT.FailedToStop) | 68
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 69
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Faulted) | 76
RCOMMENT | CM_VFD_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 77
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Stopped | OTE(UDT.STS.AtReference) | 81
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Ready | OTE(UDT.STS.Ready) | 82
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Running | OTE(UDT.STS.Active) | 83
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Accelerating | OTE(UDT.STS.Accelerating) | 84
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Decelerating | OTE(UDT.STS.Decelerating) | 85
RCOMMENT | CM_VFD_V3:AOI | Logic | STATUS: Drive Alarmed | OTE(UDT.STS.DriveAlarm) | 86
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(PIDLoop.OUT,UDT.VAL.SpeedSP) | 93
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(PIDLoop.OUT,UDT.VAL.SpeedSP) | 94
RCOMMENT | CM_VFD_V3:AOI | Logic | VALUES: Hand Speed Setpoint | MOV(0,UDT.VAL.SpeedSP) | 95
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 96
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(2,UDT.VAL.HMIState) | 97
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL RUNNING | MOV(3,UDT.VAL.HMIState) | 98
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL STOPPED | MOV(4,UDT.VAL.HMIState) | 99
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO RUNNING | MOV(5,UDT.VAL.HMIState) | 100
RCOMMENT | CM_VFD_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO STOPPED | MOV(6,UDT.VAL.HMIState) | 101
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(PIDLoop.OUT,OUT_Ref) | 102
RCOMMENT | CM_VFD_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_Ref) | 104
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 4
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 5
RCOMMENT | CM_VPRANA_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 8
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosedPos) | 9
RCOMMENT | CM_VPRANA_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 26
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 27
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 28
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 29
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 30
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 31
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 32
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 33
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 34
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SO) | 35
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 36
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 37
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SP) | 38
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 39
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 40
RCOMMENT | CM_VPRANA_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 41
RCOMMENT | CM_VPRANA_V3:AOI | Logic | STATUS$NControl Action | OTU(PIDLoop.CA) | 42
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrClosedDelay.PRE,1000,UDT.CFG.ClosedDelayTime) | 46
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 53
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 54
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 59
RCOMMENT | CM_VPRANA_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 60
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 61
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 62
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 63
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 64
RCOMMENT | CM_VPRANA_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 65
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 66
RCOMMENT | CM_VPRANA_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 67
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 68
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 69
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 72
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingOpenValve) | 74
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 75
RCOMMENT | CM_VPRANA_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 79
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 87
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 88
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 89
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 90
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 91
RCOMMENT | CM_VPRANA_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 92
RCOMMENT | CM_VPRANA_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 93
RCOMMENT | CM_VPRANA_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 95
RCOMMENT | CM_VPRANA_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 96
RCOMMENT | CM_VPRANA_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 97
RCOMMENT | CM_VPRANA_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 98
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 99
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | CPT(OUT_CV,PIDLoop.MINCV+((UDT.OUT.CV-0)/(100-0)*(PIDLoop.MAXCV-PIDLoop.MINCV))) | 100
RCOMMENT | CM_VPRANA_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 101
RCOMMENT | CM_VPRANA_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 103
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 4
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 5
RCOMMENT | CM_VPR_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 4
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 12
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosedPos) | 13
RCOMMENT | CM_VPR_V3:AOI | Logic | DEVICE SETUP Configuration of PID Instruction settings | DIV(UDT.CFG.PeriodicTaskPeriodTime,1000,PIDLoop.UPD) | 41
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KP from Loop | MOV(PIDLoop.KP,KPStorage) | 42
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KP from Loop | MOV(UDT.SET.ProportionalGain,KPStorage) | 43
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KI from Loop | MOV(PIDLoop.KI,KIStorage) | 44
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KI from Loop | MOV(UDT.SET.IntegralGain,KIStorage) | 45
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KD from Loop | MOV(PIDLoop.KD,KDStorage) | 46
RCOMMENT | CM_VPR_V3:AOI | Logic | Set KD from Loop | MOV(UDT.SET.DerivativeGain,KDStorage) | 47
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND Loop Auto Mode | OTU(PIDLoop.PVT) | 48
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND$NLoop Manual Mode | OTL(PIDLoop.PVT) | 49
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SO) | 50
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(0,PIDLoop.SO) | 51
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.SET.ManualCV,PIDLoop.SO) | 52
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | MOV(UDT.VAL.ActiveRampingSetpoint,PIDLoop.SP) | 53
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(UDT.STS.WoundUp) | 54
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTL(PIDLoop.SWM) | 55
RCOMMENT | CM_VPR_V3:AOI | Logic | SETTINGS Manual Loop Manual Control Variable | OTU(UDT.STS.WoundUp) | 56
RCOMMENT | CM_VPR_V3:AOI | Logic | STATUS$NControl Action | OTL(PIDLoop.CA) | 57
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrClosedDelay.PRE,1000,UDT.CFG.ClosedDelayTime) | 62
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 69
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 70
RCOMMENT | CM_VPR_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 75
RCOMMENT | CM_VPR_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 76
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 77
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingOpenValve) | 78
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 79
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 80
RCOMMENT | CM_VPR_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AnalogInputHiAlm) | 81
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 82
RCOMMENT | CM_VPR_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 83
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 84
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 85
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 88
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.WRK.bWorkingOpenValve) | 90
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 91
RCOMMENT | CM_VPR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 95
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 103
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 2 | MOV(2,UDT.VAL.HMIState) | 104
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 105
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 106
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 107
RCOMMENT | CM_VPR_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 108
RCOMMENT | CM_VPR_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 109
RCOMMENT | CM_VPR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 111
RCOMMENT | CM_VPR_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 112
RCOMMENT | CM_VPR_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 113
RCOMMENT | CM_VPR_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 114
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 1 Energize/De-energize | OTE(OUT_Solenoid) | 115
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | CPT(OUT_CV,PIDLoop.MINCV+((UDT.OUT.CV-0)/(100-0)*(PIDLoop.MAXCV-PIDLoop.MINCV))) | 116
RCOMMENT | CM_VPR_V3:AOI | Logic | OUTPUT: Output 2 Energize/De-energize | MOV(0,OUT_CV) | 117
RCOMMENT | CM_VPR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 120
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 0
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 3
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 4
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 5
RCOMMENT | CM_VSL_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 6
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 4
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 5
RCOMMENT | CM_VSL_V3:AOI | Logic | STATUS: Open Status | OTE(UDT.STS.InOpenPos) | 12
RCOMMENT | CM_VSL_V3:AOI | Logic | STATUS: Closed Status | OTE(UDT.STS.InClosePos) | 13
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrCloseDelay.PRE,1000,UDT.CFG.CloseDelayTime) | 17
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 24
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.AutoResltCntrl) | 25
RCOMMENT | CM_VSL_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 30
RCOMMENT | CM_VSL_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 31
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Auto Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 32
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Manual Open/Close | OTU(UDT.WRK.bWorkingEngValve) | 33
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 34
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 35
RCOMMENT | CM_VSL_V3:AOI | Logic | COMMAND: Fault Reset | OTU(UDT.FLT.AutoCMDWhileInMan) | 36
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Failed to Open, Failed to Close, Feedback Fault Check | OTE(UDT.WRK.bBothLSStuckOn) | 37
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER: Fault Timer | TON(UDT.WRK.tmrFaultDelay,?,?) | 38
RCOMMENT | CM_VSL_V3:AOI | Logic | TIMER: Fault Timer | ADD(UDT.VAL.TimeToClose,0.5,UDT.VAL.TimeToClose) | 39
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Failed to Open Fault, Failed to Close Fault, Illegal Feedback Fault | OTL(UDT.FLT.IllegalFeedback) | 40
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 41
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 44
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.WRK.bWorkingEngValve) | 46
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 47
RCOMMENT | CM_VSL_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 51
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGE | MOV(1,UDT.VAL.HMIState) | 59
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL OPEN | MOV(3,UDT.VAL.HMIState) | 61
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 4 MANUAL CLOSED | MOV(4,UDT.VAL.HMIState) | 62
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO OPEN | MOV(5,UDT.VAL.HMIState) | 63
RCOMMENT | CM_VSL_V3:AOI | Logic | HMI Device Status: STATE 6 AUTO CLOSED | MOV(6,UDT.VAL.HMIState) | 64
RCOMMENT | CM_VSL_V3:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 65
RCOMMENT | CM_VSL_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],UDT.WRK.AutoResltCntrl.LEN) | 67
RCOMMENT | CM_VSL_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 68
RCOMMENT | CM_VSL_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 69
RCOMMENT | CM_VSL_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 70
RCOMMENT | CM_VSL_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out1) | 71
RCOMMENT | CM_VSL_V3:AOI | Logic | OUTPUT STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(OUT_Out2) | 72
RCOMMENT | CM_VSL_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],UDT.WRK.InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 73
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WSGE_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_WSGE_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_WSGE_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_WSGE_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 18
RCOMMENT | CM_WSGE_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 24
RCOMMENT | CM_WSGE_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 25
RCOMMENT | CM_WSGE_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 26
RCOMMENT | CM_WSGE_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_LocalInterlock) | 27
RCOMMENT | CM_WSGE_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 28
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.INOUT.ModuleStatus) | 0
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 1
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.STS.Mode) | 3
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 4
RCOMMENT | CM_WSP_V3:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],0,UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 5
RCOMMENT | CM_WSP_V3:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | CM_WSP_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 2
RCOMMENT | CM_WSP_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 3
RCOMMENT | CM_WSP_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 11
RCOMMENT | CM_WSP_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.VAL.InUseBy[0],InUseSize) | 17
RCOMMENT | CM_WSP_V3:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | FLL(0,UDT.CMD.AutoTare[0],CMDSize) | 18
RCOMMENT | CM_WSP_V3:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 19
RCOMMENT | CM_WSP_V3:AOI | Logic | MODE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Mode) | 20
RCOMMENT | CM_WSP_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (InUseByAOI[1],UDT.VAL.InUseBy[1],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.INOUT.ModuleStatus,ProdLink,UDT.VAL.InUseByType[1],UDT.VAL.InUseByID[1],InUseByAOI[1].UserPriority,UDT.VAL.InUseByTypeArray[1]) | 21
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | CM_WS_V3:AOI | Logic | CONNECTIONS | MOV(IN_RawWeight,UDT.IN.RawWeight) | 0
RCOMMENT | CM_WS_V3:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 2
RCOMMENT | CM_WS_V3:AOI | Logic | TIMER PRESETS | MOV(30,UDT.CFG.SIMWeighTime) | 5
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Control Module Fault | RES(AutoResltCntrl) | 11
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Control Module Fault | RES(AutoResltCntrl) | 12
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: In Use | OTL(UDT.STS.InUse) | 15
RCOMMENT | CM_WS_V3:AOI | Logic | Number of Cycles | CLR(UDT.VAL.NumOfCycles) | 17
RCOMMENT | CM_WS_V3:AOI | Logic | Number of Cycles | ADD(UDT.VAL.NumOfCycles,1,UDT.VAL.NumOfCycles) | 18
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[1],InUseBy1) | 19
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Auto Gain/Loss | OTL(UDT.INOUT.bLossWeight) | 20
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Start/Stop Gain In Weight STATUS: Weigh Up In Progress STATUS: Gain In Weight Active | OTU(UDT.STS.StabComplete) | 22
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Start/Stop Loss In Weight STATUS: Weigh Up In Progress STATUS: Loss In Weight Active | OTU(UDT.STS.StabComplete) | 23
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Auto/Manual Zero | MOV(UDT.SET.Preact,UDT.VAL.Preact) | 24
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Settle | MOV(UDT.SET.SIM,UDT.VAL.TareWeight) | 25
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Stop | OTL(UDT.STS.Stopping) | 26
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Stabilize | OTU(UDT.STS.Stopping) | 27
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Analog Alarms Enabled | OTU(UDT.STS.AlarmEnabled) | 28
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Gain in Weight Weigh Up Complete ACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 29
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Loss in Weight Weigh Up Complete ACTUAL = (SETPOINT - PREACT) | OTL(UDT.STS.Complete) | 30
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS: Zero Deadband Status | OTE(UDT.STS.Zeroed) | 31
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Tare Weight Reading | SUB(UDT.VAL.ActualWeight,UDT.VAL.TareWeight,UDT.VAL.NetWeight) | 32
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Gain In Weight Amount Remaining | SUB(UDT.VAL.Setpoint,UDT.VAL.NetWeight,UDT.VAL.AmountRemain) | 33
RCOMMENT | CM_WS_V3:AOI | Logic | VALUE: Loss In Weight Amount Remaining | ADD(UDT.VAL.Setpoint,UDT.VAL.NetWeight,UDT.VAL.AmountRemain) | 34
RCOMMENT | CM_WS_V3:AOI | Logic | UDT.IN.SIMULATION TIMER | CPT(UDT.VAL.ActualWeight,UDT.IN.RawWeight/(UDT.CFG.RawUnitsHi-UDT.CFG.RawUnitsLo)*(UDT.CFG.EngUnitsHi-UDT.CFG.EngUnitsLo)) | 35
RCOMMENT | CM_WS_V3:AOI | Logic | CALCULATE DELTA | MOV(UDT.VAL.ActualWeight,rTotalPreviousScan) | 36
RCOMMENT | CM_WS_V3:AOI | Logic | CALCULATE DELTA | OTU(FlowRateCTL.DN) | 37
RCOMMENT | CM_WS_V3:AOI | Logic | Input: Mass Flow Rate | RES(tmrFlowRateAcc) | 38
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(ProdZoneFltReset) | 45
RCOMMENT | CM_WS_V3:AOI | Logic | COMMAND: Fault Reset | OTU(ExternalFault) | 46
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: HI/LO Fault Timer | TON(tmrLowFlow,?,?) | 47
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & WARNING: Low Flow Fault | OTL(UDT.FLT.LoFlow) | 48
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.Interlock) | 49
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: HI Fault Timer | TON(tmrHiFaultDelay,?,?) | 50
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: LO Fault Timer | TON(tmrLoFaultDelay,?,?) | 51
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & FAULT: Hi$N | OTL(UDT.FLT.Hi) | 52
RCOMMENT | CM_WS_V3:AOI | Logic | STATUS & FAULT: Lo | OTL(UDT.FLT.Lo) | 53
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Mode Faults | OTL(UDT.FLT.AutoCMDWhileInMan) | 55
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 56
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.SingleScanDelta) | 58
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Fault Code Generation | OTL(UDT.STS.Stopping) | 62
RCOMMENT | CM_WS_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,FaultCodeHolding) | 63
RCOMMENT | CM_WS_V3:AOI | Logic | ZoneFault Signal: Signal to All Members of the Zone That a Fault Exists on a CM$N | OTL(ZoneLink.FaultExists) | 66
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 70
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 2 WARNING | MOV(2,UDT.VAL.HMIState) | 71
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 3 MANUAL MODE | MOV(3,UDT.VAL.HMIState) | 72
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 4 | MOV(4,UDT.VAL.HMIState) | 73
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 5 AUTO MODE | MOV(5,UDT.VAL.HMIState) | 74
RCOMMENT | CM_WS_V3:AOI | Logic | HMI Device Status: STATE 6 | MOV(6,UDT.VAL.HMIState) | 75
RCOMMENT | CM_WS_V3:AOI | Prescan | CALCULATE DELTA | OTL(UDT.STS.Stopping) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 47
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 48
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 49
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 60
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 61
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 67
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 70
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 71
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | Clear Registers | MOV(10,UDT.SET.NextStateNumber) | 72
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NIf Automated Top Valve, Goto 1110 to Evaluate Logic$NIf Manual Type Top Valve, Goto 11080 to Prompt Operator to Open Vavle$N$N************************************************************************************************ | MOV(11080,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NIf Automated Bottom Valve, Goto 1150 to Evaluate Logic$NIf Manual Type Bottom Valve, Goto 11090 to Prompt Operator to Open Vavle$N$N************************************************************************************************ | MOV(11090,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$NAutomated Top Inlet Valve Logic$N$N************************************************************************************************ | MOV(11081,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$NAutomated Bottom Inlet Valve Logic$N$N************************************************************************************************ | OTE(BotInletValve.CMD.AutoOpen[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 85
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 87
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | **************************************************************************************************$N$NClear the Container that was Added to the Add Pot Then goto Complete$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 88
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Destination$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 107
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate Destination Scan$N11120 = Wrong Destination Scanned$N11055 = Matching Destination$N**************************************************************************************************** | CLR(UDT.PMT.PromptType) | 108
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Intermediate Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 109
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate Intermediate Container Scan$NCopy Scan Value to Val.Cont$N$N**************************************************************************************************** | MOV(11060,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Matches$N11065 = If BatchID and Destination Match, Search For RM$N11121 = Container Match but Mismatch BatchID$N11122 = Container Match but Mismatch Destination$N**************************************************************************************************** | MOV(11122,UDT.SET.NextStateNumber) | 111
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Not Found, Add one to the Index$N$N11123 = Container Not Found$N**************************************************************************************************** | JMP(ContSearch) | 112
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NIf Raw Material Is Found In Container$N1080 = Evaluate the Add Pot Top Type, If Manual goto 11080, If Automated goto 1110$N11124 = Raw Material Match but Wrong Item Number$N**************************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$N11125 = RM Not Found$N$N**************************************************************************************************** | JMP(RMSearch) | 114
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NManual Type Top Inlet Valve$N$NPrompt Operator to Open Top Inlet Valve and Acknolwedge When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 115
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NAutomated Type Top Inlet Valve$N$NPrompt Operator to Charge RM and Acknolwedge When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 117
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | ****************************************************************************************************$N$NManual Type Bottom Inlet Valve$N$NPrompt Operator to Open Bottom Inlet Valve and Acknolwedge When Complete$N$N1200 = Move Values to VAL$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 119
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 121
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 123
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 125
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Not Found$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 127
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Item Number Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 129
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container RM Not In Container$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 131
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 134
RCOMMENT | EM_ADDPOT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 137
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 8
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 15
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 16
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 17
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 26
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 55
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 56
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 76
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 77
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 83
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.VAL.OriginalSetpoint,PrevSetpoint) | 87
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 89
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | CLR(UDT.SET.MixTime) | 123
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Running$N1000-4999 | OTE(UDT.STS.InSetpointSpeed) | 144
RCOMMENT | EM_AGIT_M2S_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 172
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Sets the Production Link Type and ID | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 8
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 9
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Move InUseBy Value To Usable Indirect Register$N | MOV(UDT.VAL.InUseBy[1],UDT.WRK.InUseBy1) | 12
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | TIMER PRESETS | MOV(60000,tmrAutoRestartFail.PRE) | 15
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | COMMAND: Auto/Manual | OTU(UDT.STS.Mode) | 16
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 17
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | $N | OTL(UDT.STS.Aborted) | 26
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 55
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 56
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 76
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 77
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 83
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(6000,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(UDT.SET.MyTankNumber,UDT.VAL.MyTankNumber) | 87
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Running$N1000-4999 | MOV(0,UDT.VAL.PrevMode) | 89
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Running$N1000-4999 | CLR(UDT.SET.MixTime) | 124
RCOMMENT | EM_AGIT_VFD_V3:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 178
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CoFeed_V2W_V2W_V3:AOI | Logic | Set In Service Bits | OTE(UDT.WRK.Delivery_A_ValveInService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CoFeed_V2W_V2W_V4:AOI | Logic | Set In Service Bits | OTE(UDT.WRK.Delivery_A_ValveInService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | 51= $QReady to Charge Material $Q$N52= $Q To $Q$N53= $Q. Scan Material Int. Container.$Q$NMessage1= $QReady to Charge Material XXX To YYY. Scan Material Int. Container.$Q | MOV(11050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NLoop Through Scale to Find Matching Scanned Scale to get ScaleIndex$N$N11128 = If Not Found Prompt Operator$N11050 = Prompt Operator if they are Ready To Start$N$N************************************************************************************************ | MOV(11068,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf the Container has Multiple RM$'s in it then Remove the RM that was Required, $Nand Mark the Container as Being Added.$N$N11095 = Prompt For Next Container or Finished Prompt$N$N************************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NVerify No Other Containers Match BatchID, ItemNo, RM$N$N****************************************************************************************************** | MOV(11106,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************************************************$N$NSearch For a Matching Container$N$N11060 = Match Found$N11121 = Found but Batch ID Mismatch$N$N****************************************************************************************************************************************** | MOV(11121,UDT.SET.NextStateNumber) | 114
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****$NIf ContIndex Goes Above 50, Go to Error $QInt. Container Not Found$Q$N11120$N$N***** | MOV(11120,UDT.SET.NextStateNumber) | 115
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************************************************$N$NSearch For Material in Scaned Container$N$N****************************************************************************************************************************************** | SUB(RM_Size,1,RM_Offset) | 116
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NIf Raw Material Is Found In Container$N11065 = Scan Destination Container$N11124 = Raw Material Match but Wrong Item Number$N**************************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 117
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$N11122 = RM Not Found$N$N**************************************************************************************************** | MOV(11122,UDT.SET.NextStateNumber) | 118
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************$N$NFound the Container and RM in the Container and everything Matches. $NNow Scan Vessel to verify Match$N$N11070 = Once Destination is Scanned Prompt to Scan Destination When Complete$N$NIf Container has Already Been Added to Vessel, Then Move to Clear Container$N11080$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 119
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ******************************************************************************************************$N$NPrompt Operator if they Want to Reweigh the Intermediate Containers. The Selection$Non First Pass, it will stay until EM Completes$N$N11067 - Prompt Operator to Scan Scale For Reweigh$N$N11070 = Once Destination is Scanned Prompt to Scan Destination When Complete$N$N**************************************************************************************************** | MOV(2,UDT.PMT.PromptType) | 120
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 124
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11069 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.PromptRealEntry) | 125
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | ****************************************************************************************************$NReweigh $N$NPrompt Operator to Place Container On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 126
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$NScan Destination Vessel/PreMix$NIf Match$N11075 = Prompt For Second Scan for Complete$NIf Doesnt Match$N11123 = Wrong Destination Scanned$N$N************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 128
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NPrompt to Scan When Complete, When Scan is Completed move to final Values$NTo VAL locations$N$N************************************************************************************************** | MOV(11085,UDT.SET.NextStateNumber) | 130
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf not a Multiple RM Container, then Clear Data From Container to allow it to be Used$Nfor another Addition. If it is a Multiple RM, then go to 11058 to Remove that Element. If it $Nis a Multiple RM and It has already been marked as Added, then Clear Data.$N$N1090 = Remove Added RM from Container, Mark As Added$N11095 = Prompt For Next Container or Finished$N$N************************************************************************************************** | MOV(1090,UDT.SET.NextStateNumber) | 131
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NCreate String Entry Prompt For Operator to Select $QNext Container$Q or $QFinished$Q$NThen Move to 11100 to Process the Selection$N$N************************************************************************************************** | MOV(11100,UDT.SET.NextStateNumber) | 132
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | **************************************************************************************************$N$NIf $QNext Container$Q Selected Move to 1050 To Start Over Again$N$NIf $QFinished$Q Selected Move to 11105 to Finish $N$N************************************************************************************************** | MOV(0,UDT.PMT.PromptType) | 133
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NSearch Through Containers to Find a Matching BatchID.$N11107 = If Found Matching BatchID - Look at RM & ItemNo$N11110 = Clean Up No Other Containers Match$N$N****************************************************************************************************** | MOV(11107,UDT.SET.NextStateNumber) | 134
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NSearch Through Raw Materials of Container to Find a Matching Item Number and RM Code$N11108 = If Found Matching ItemNo and RM_Code, Prompt Operator if they are Finished$N11110 = Clean Up No Other Containers Match$N$N****************************************************************************************************** | MOV(11108,UDT.SET.NextStateNumber) | 136
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NFinish any Clean up then Go Complete$N9500$N$N****************************************************************************************************** | MOV(9500,UDT.SET.NextStateNumber) | 139
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NIf No Container Is Found Prompt$NOperator $N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 140
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NIf Container Found But Wrong BatchID Prompt$NOperator $N$N1050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 142
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$N Raw Material Is Not Found in Container Prompt$NOperator $N$N11050 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 144
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *******************************************************************************************************$N$NWrong Destination Barcode Scanned$NPrompt Operator of Error, Then Prompt to Scan$N$N11065 = Scan Destination Vessel/PreMix$N$N*********************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 146
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *******************************************************************************************************$N$NCorrect Raw Material but Wrong Item Number In Container$NPrompt Operator of Error, Then Prompt to Scan Another Container$N$N1050 = Scan Destination Vessel/PreMix$N$N*********************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 148
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 150
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 154
RCOMMENT | EM_CONT_DLY_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 157
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 0
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.FLT.Custom.0) | 17
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | This routine executes the following generic paint logic :$NWW Density Alarming, Solids Calculations, Required Yield Var Hit, Rework Hit | OTE(UDT.STS.GP.WWInitialFlushComplete) | 24
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | WW Vol GP = (( WW Density - 8.31) / 2.34 ) * WW Vol Deliv$NWhere : $T$NWW Density = Totalized WW Mass Delivered / Totalized WW Volume Delivered$N8.31 = Density of Water$N2.34 = 10.65 - 8.31 (Assumed Density of Paint - Density of Water)$NWW Vol Deliv = Totalized WW Volume Delivered | CPT(UDT.VAL.GP.GP_Volume_Actual,(UDT.VAL.GP.WW_Density-UDT.SET.GP.Water_Density)/(UDT.SET.GP.WW_Density-UDT.SET.GP.Water_Density)*UDT.VAL.GP.Volume_Actual) | 29
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | MOV(0,UDT.VAL.GP.WWDoneReason) | 30
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.STS.GP.WWDone) | 31
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Yield Var Hit (lbs) = Volume of GP Added * 8.31 (Density of Water) | MUL(UDT.VAL.GP.GP_Volume_Actual,UDT.SET.GP.WW_Density,UDT.VAL.GP.GP_Mass_Actual) | 32
RCOMMENT | EM_DGP_V2W_AOD_PMPALL_R_V4:AOI | Logic | Rework Volume Hit = GP max Volume - Volume of GP delivered | CLR(UDT.VAL.GP.RW_Volume_Setpoint) | 36
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 0
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.FLT.Custom.0) | 13
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | This routine executes the following generic paint logic :$NWW Density Alarming, Solids Calculations, Required Yield Var Hit, Rework Hit | OTE(UDT.STS.GP.WWInitialFlushComplete) | 20
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | WW Vol GP = (( WW Density - 8.31) / 2.34 ) * WW Vol Deliv$NWhere : $T$NWW Density = Totalized WW Mass Delivered / Totalized WW Volume Delivered$N8.31 = Density of Water$N2.34 = 10.65 - 8.31 (Assumed Density of Paint - Density of Water)$NWW Vol Deliv = Totalized WW Volume Delivered | CPT(UDT.VAL.GP.GP_Volume_Actual,(UDT.VAL.GP.WW_Density-UDT.SET.GP.Water_Density)/(UDT.SET.GP.WW_Density-UDT.SET.GP.Water_Density)*UDT.VAL.GP.Volume_Actual) | 25
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | MOV(0,UDT.VAL.GP.WWDoneReason) | 26
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | When the Volume of GP Delivered > GP Max or the WW tank reads low level the Delivery of WW is complete. | OTL(UDT.STS.GP.WWDone) | 27
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Yield Var Hit (lbs) = Volume of GP Added * 8.31 (Density of Water) | MUL(UDT.VAL.GP.GP_Volume_Actual,UDT.SET.GP.WW_Density,UDT.VAL.GP.GP_Mass_Actual) | 28
RCOMMENT | EM_DGP_V2W_AOD_R_V4:AOI | Logic | Rework Volume Hit = GP max Volume - Volume of GP delivered | CLR(UDT.VAL.GP.RW_Volume_Setpoint) | 32
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 82
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11124,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 85
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 86
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | MOV(11050,UDT.SET.NextStateNumber) | 88
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NIf Preweigh is a Bulk Storage Type goto 11075, Otherwise goto 11060$N11075 will utilize Valves and Pumps From Bulk Storage to Scale$N11060 will utilize Operator Additions to a Container on the Scale$N$N************************************************************************************************ | MOV(11060,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NAfter Scanning in Container and Raw Material Information Store Information$Nin the Container User Defined Structure$N$NOnce Stored Continue on with Logic to have Operator Setup the Scale 11085$N$N********************************************************************************************** | MOV(1090,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(1120,UDT.SET.NextStateNumber) | 93
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 101
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.TOLERANCE,EM_DLY[DLYIndex].SET.TolerancePCT) | 108
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint | MOV(11100,UDT.SET.NextStateNumber) | 109
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N************************************************************************************************ | MOV(UDT.WRK.UserBit,SCALE[ScaleIndex].VAL.InUseBy[0]) | 110
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N************************************************************************************************ | MOV(UDT.WRK.UserBit,SCALE[ScaleIndex].VAL.InUseBy[0]) | 111
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1200,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 114
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 115
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 134
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 135
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 136
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 137
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 138
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$N11060 = Batch IDs Match Continue Logic$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | MOV(0,UDT.PMT.PromptType) | 139
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11065 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 140
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 142
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Intermediate Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 144
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Matches$N1080 = Container Is Empty$N11080 = Container has BatchID, Prompt to Use Same Container$N11126 = Container Match but Mismatch BatchID$N11125 = Container Match but Mismatch Destination$N**************************************************************************************************** | MOV(11126,UDT.SET.NextStateNumber) | 146
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NIf Container Not Found, Add one to the Index$N$N11123 = Container Not Found$N**************************************************************************************************** | JMP(ContSearch) | 147
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator Container Already Being Used, Want to Add To It?$N11081 - Add to the Container that has Something in it$N11075 - Rescan Intermediate Container$N$N************************************************************************************************** | MOV(2,UDT.PMT.PromptType) | 148
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | 1=Yes$N2=No | CLR(UDT.PMT.Message2.LEN) | 149
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NSearch For RM in Container that is not Empty. $NLook for the same RM_Code to add to that element$NIf same RM_Code is not in there then add to the Container in the next Open $NElement. Also mark Container and MultiRM.$NIf a RM_Code is Matched and the ItemNo is different set error to Scan another container$N**************************************************************************************************** | MOV(11127,UDT.SET.NextStateNumber) | 150
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$NIf neither a blank or matching RM_Code exists then set a gnernal Error to$NScan another Continer$N11123 = Container Error$N$N**************************************************************************************************** | JMP(RMSearch) | 151
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11100 - Prompt For Next Cont. or Finished$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 153
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NInt. Container Not Found$N11075 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NDestinatino Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof Destination$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof BatchID$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NUsing a Multi-Raw Material Container, the Scanned Container Has a Mismatch$Nof ItemNumber$N$N11075 = Scan Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 185
RCOMMENT | EM_DLY_PREWEIGH_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 188
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 81
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | OTU(UDT.WRK.ChangeScale) | 87
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NAfter the Operators Places the Empty Pallet On the Scale and Scans$NGet weight, Subtract the Final Weight From the Initial Weight to Get the Charged$NWeight.$NIf this is the First RM Charge/Lot Number, then place it in VAL.Cont[0].$NIf this is the >0 charge check to see if the current charge has the same Lot/RM as$Nthe Previous. If it is the same then add to it if not add it ot the next Open Cont.$N$N$N********************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(11094,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 100
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.Mode,EM_DLY[DLYIndex].SET.Mode) | 107
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint$N$NAFI on second branch, was added to allow tracking of the actual during a delivery and not just totalize$Nthe value at the end of a delivery. The rung above it is where the calculation is being done now. | MOV(11096,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N11105 - Over Weight Tolerance, Ask For Reweigh or Supervisors Approval$N11065 - Weight Within Tolerance, Prompt Operator to Scan Raw Materail$N$NReAquire Scale $N$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 111
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N11106 - Over Weight Tolerance, Prompt Operator For Reweigh or Supervisors Approval$N11105 - Under Weight Tolerance, Ask if they Want to add Another Container or Continue with Supervisors Approval$N1200 - Weight In Tolerance, Continue to Cleanup$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 112
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1194,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 121
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 122
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 141
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 142
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 143
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 144
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 145
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$NIf a Manual Charge, that means there has to be a Hatch and a barcode to scan for the $Ndestination. If it is an auto charge, then we dont have to scan the destination barcode.$N11060 = Batch IDs Match Continue Logic - Scan Destination$N11065 - Batch IDs Match but Auto Charge - RM Code$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 146
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NScan Destination Location$N11065 - Scan Material Code$N11125 - Destination Not Found$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 147
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11070 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 149
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 152
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11080 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 155
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Charge Material X to Vessel Y and Scan Hatch When Complete$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet Back On Scale and Scan Get Weight$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(1141,UDT.SET.NextStateNumber) | 169
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Blow Down Line, Confirm When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | ****************************************************************************************************$N$NOperator Confirms Line Is Blown Down.$N**************************************************************************************************** | MOV(1196,UDT.SET.NextStateNumber) | 171
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11060 = Scan Destination$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 184
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 186
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 188
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 191
RCOMMENT | EM_DLY_SCALE_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 194
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Clear Registers | CLR(UDT.VAL.ExpMfgDate.LEN) | 70
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Check Setpoints | MOV(100,UDT.SET.NextStateNumber) | 73
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Tank Needed in the EM_Status$N$N********************************************************************************************** | MOV(11040,UDT.SET.NextStateNumber) | 81
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(1050,UDT.SET.NextStateNumber) | 83
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the Matching Scale Needed in the EM_Scale$N$N********************************************************************************************** | MOV(11128,UDT.SET.NextStateNumber) | 84
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **********************************************************************************************$N$NFind the EM_DLY needed if the Preweigh is a Bulk Storage Type$N$N********************************************************************************************** | OTU(UDT.WRK.ChangeScale) | 87
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NAfter the Operators Places the Empty Pallet On the Scale and Scans$NGet weight, Subtract the Final Weight From the Initial Weight to Get the Charged$NWeight.$NIf this is the First RM Charge/Lot Number, then place it in VAL.Cont[0].$NIf this is the >0 charge check to see if the current charge has the same Lot/RM as$Nthe Previous. If it is the same then add to it if not add it ot the next Open Cont.$N$N$N********************************************************************************************** | MOV(11095,UDT.SET.NextStateNumber) | 90
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NEM_DLY Logic to control the Acquired EM_DLY$N$N************************************************************************************************ | MOV(11094,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Look at this Rung Later. It is Rung 28 in the EI_DLY_AOI_V4 | OTL(EM_DLY[DLYIndex].CMD.Abort) | 100
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Rung 47 in the EI_DLY_AOI_V4 - it is pass many more values that i am not.$NWe can add these to the EM_DLY_Preweigh UDT to allow this but not sure $Nhow they will get populated, FTBatch or HMI Screen$N$NDetermining What Setpoint we send the EM_DLY.$NIf ActiveSetpoint is Greater than the MaxWeight of the Container, Calculate the Amount we can Add to it and use that as the Setpoint for The EM_DLY$NIf the Container MaxWeigh-Amount is Greater than the ActiveSetpoint, then Move the Active Setpoint to the EM_DLY Setpoint$NIf the ActiveSetpoint is greater than the MaxWeight, make sure the Available weight is less than the Active Setpoint, then move available amount to the EM_DLY Setpoint$N$N | MOV(UDT.SET.Mode,EM_DLY[DLYIndex].SET.Mode) | 107
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | Upon the Completion of the Delivery, Move the Final amount to the Total Amount. $NAlso update the Active Setpoint, Which will be amount Remaining From the Original Setpoint$N$NAFI on second branch, was added to allow tracking of the actual during a delivery and not just totalize$Nthe value at the end of a delivery. The rung above it is where the calculation is being done now. | MOV(11096,UDT.SET.NextStateNumber) | 110
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NOperator Scanned the Next Container After Complete.$NCheck to see if Weight is High Over Tolerance. If it is Request a Reweigh by$NSetting the Actual amount in Container to 0 and having the operator re-weigh$Nthe product.$N$N11105 - Over Weight Tolerance, Ask For Reweigh or Supervisors Approval$N11065 - Weight Within Tolerance, Prompt Operator to Scan Raw Materail$N$NReAquire Scale $N$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 111
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NOperator Scanned Finished, the system will check Weights to be sure they are$Nnot Overweight. If Overweight they will need to Re-Weigh or get Supervisors$NApproval.$NIf Underweight, Prompt to add more Material or Supervisors Approval.$N$N11106 - Over Weight Tolerance, Prompt Operator For Reweigh or Supervisors Approval$N11105 - Under Weight Tolerance, Ask if they Want to add Another Container or Continue with Supervisors Approval$N1200 - Weight In Tolerance, Continue to Cleanup$N************************************************************************************************ | OTU(SCALE[ScaleIndex].CMD.AutoLoss[UDT.WRK.UserWord].[UDT.WRK.UserBit]) | 112
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NRelease Scale$N$N************************************************************************************************ | MOV(1194,UDT.SET.NextStateNumber) | 113
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NMove Variables to the Val structure for FTBatch$N$N************************************************************************************************ | MOV(1250,UDT.SET.NextStateNumber) | 121
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | **************************************************************************************************$N$NCleanup$N$N************************************************************************************************ | MOV(9500,UDT.SET.NextStateNumber) | 122
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Scale they want to Use. $NOnly Call this step if No Scale was in the UDT.SET$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 141
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$N$N**************************************************************************************************** | MOV(1040,UDT.SET.NextStateNumber) | 142
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 143
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(11055,UDT.SET.NextStateNumber) | 144
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Batch ID$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 145
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NEvaluate BatchID Scan$NIf a Manual Charge, that means there has to be a Hatch and a barcode to scan for the $Ndestination. If it is an auto charge, then we dont have to scan the destination barcode.$N11060 = Batch IDs Match Continue Logic - Scan Destination$N11065 - Batch IDs Match but Auto Charge - RM Code$N11121 = Batch ID Mismatch$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 146
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NScan Destination Location$N11065 - Scan Material Code$N11125 - Destination Not Found$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 147
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Material Code on Bag/Container$N$N11070 - Scan Lot Number$N11122 - Incorrect Raw Material Scanned$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 149
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Lot Number on Bag/Container$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 152
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 154
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Tare Scale$N11080 - Prompt Operator to Place Pallet On Scale, then Get Weight$N$N**************************************************************************************************** | CLR(UDT.PMT.Message2.LEN) | 155
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Scan Start Bulk Delivery$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 156
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet On Scale, Then Get Weight$N$NMove Scales Mass Total into the Wrk.GetWeight$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 158
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Charge Material X to Vessel Y and Scan Hatch When Complete$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 160
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$NSource Type 2$N$NPrompt Operator to Place Pallet Back On Scale and Scan Get Weight$N$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 162
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 164
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator for Next Cont. or Finished$N1140 - Store results $N1141 - Store Results and Evaulate Final Amounts$N$N**************************************************************************************************** | MOV(4,UDT.PMT.PromptType) | 166
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator if they are ready to Pre-weigh Material X at Scale Y $N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 168
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Acknowledges Ready to Pre-Weigh Material at Scale$N**************************************************************************************************** | MOV(1141,UDT.SET.NextStateNumber) | 169
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NPrompt Operator to Blow Down Line, Confirm When Complete$N$N**************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 170
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | ****************************************************************************************************$N$NOperator Confirms Line Is Blown Down.$N**************************************************************************************************** | MOV(1196,UDT.SET.NextStateNumber) | 171
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Underweight $NCondition$N$NResponse = 1 = 1140 - Another Addition$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 172
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NPrompt Operator For a ReWeigh or Supervisors Approval For Overweight $NCondition$N$NResponse = 1 = 11095 = Reweigh$NResponse = 2 = 1200 - Cleanup$N$N****************************************************************************************************** | MOV(6,UDT.PMT.PromptType) | 174
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NScale In Use Prompt$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 176
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NBatchID Mismatch$N$N11055 = Scan Int. Container$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 178
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Material Code Scanned$N$N11060 = Scan RM Code $N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 180
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Destination Scanned$N$N11060 = Scan Destination$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 182
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NScale Not Found$N$N6000 = Abort Cause there was not Operator Action to Fix$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 184
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NWrong Scale Scanned$N$N11085 = Scan Scale$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 186
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | *****************************************************************************************************$N$NBulk Storage Tank Not Found$N$N6000 = Abort$N$N****************************************************************************************************** | MOV(1,UDT.PMT.PromptType) | 188
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 191
RCOMMENT | EM_DLY_SCALE_V2:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 194
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_CHASE_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PMPALL_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_PURGE_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_DPH_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_DPH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_PMR_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V2W_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V3W_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_V3W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_2SCH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_CH_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VDB_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_SADD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 4
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_PMPALL_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_PMPALL_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_R_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_DLY_VPR_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_HOLD_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_HOLD_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_HOLD_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_HOLD_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_HOLD_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_HOLD_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_HOLD_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_HOLD_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_HOLD_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_HOLD_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 100
RCOMMENT | EM_HOLD_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 103
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_PMPT_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_PMPT_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_PMPT_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_PMPT_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_PMPT_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_PMPT_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_PMPT_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_PMPT_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_PMPT_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_PMPT_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 112
RCOMMENT | EM_PMPT_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 115
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_QC_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EM_QC_V1:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 2
RCOMMENT | EM_QC_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 8
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[4],UDT.WRK.InUseBy4) | 14
RCOMMENT | EM_QC_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTE(UDT.WRK.ProdZoneFltReset) | 45
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 46
RCOMMENT | EM_QC_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 47
RCOMMENT | EM_QC_V1:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 58
RCOMMENT | EM_QC_V1:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.HOLD) | 59
RCOMMENT | EM_QC_V1:AOI | Logic | HOLDING LOGIC - Shutdown Logic$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(5110,UDT.SET.NextStateNumber) | 65
RCOMMENT | EM_QC_V1:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(9500,UDT.SET.NextStateNumber) | 68
RCOMMENT | EM_QC_V1:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 69
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[4],UDT.VAL.InUseBy[4],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[4],UDT.VAL.InUseByID[4],UDT.WRK.InUseByAOI[4].UserPriority,UDT.VAL.InUseByTypeArray[4]) | 107
RCOMMENT | EM_QC_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 110
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_QD_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_AOD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_M2S_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RECIRC_V2W_VFD_V3:AOI | Logic | Set In Service Bits | OTE(UDT_DLY.HDR1InService) | 5
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Resource Arbitration Manager$N$NThis routine will coordinate which unit currently owns a resource.$N | NOP() | 0
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | TIMER PRESETS | MOV(FP,UDT.REV.FP) | 1
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,ProdLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 3
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Copy Unique Input INDEX to Buffered Location for Code Execution | JMP(Disabled) | 7
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | QUEUING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.CMD.ClearQueue) | 11
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.FSC_CONTROL_1) | 12
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | FLL(0,UDT.WRK.InUseRef[0],UDT.WRK.CMDAutoDINT) | 13
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTU(UDT.WRK.bLoadQueueBuffer) | 14
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Check to see if Request ID has already been loaded into the Que | MOV(UDT.WRK.QueueBuffer[0],UDT.WRK.QueueUnload) | 16
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Check to see if Request ID has already been loaded into the Que | RES(UDT.WRK.FSC_CONTROL_1) | 17
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | MOV(UDT.WRK.QueuePrioritySize,UDT.WRK.QueueUnloadControl.LEN) | 18
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | RES(UDT.WRK.QueueUnloadControl) | 19
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | MOV(UDT.WRK.QueuePrioritySize,UDT.WRK.QueueLoadControl.LEN) | 20
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Load Request ID into | RES(UDT.WRK.QueueLoadControl) | 21
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | CLR(UDT.SET.ReqNextPathNumber) | 24
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(UDT.VAL.CurrentUser,UDT.WRK.LSCurrentUser) | 31
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | TIMER PRESETS | MOV(3000,UDT.WRK.tmrFaultReset.PRE) | 33
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | FLL(0,UDT.VAL.InUseBy[0],5) | 34
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | COMMAND: Auto Open/Close | OTL(UDT.WRK.Enable) | 41
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(IN_USE) | 64
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(IN_QUEUE) | 65
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(0,UDT.VAL.HMIState) | 66
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(2,UDT.VAL.HMIState) | 67
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(1,UDT.VAL.HMIState) | 68
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(6,UDT.VAL.HMIState) | 69
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(3,UDT.VAL.HMIState) | 70
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Chase Active | MOV(7,UDT.VAL.HMIState) | 71
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(4,UDT.VAL.HMIState) | 72
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(5,UDT.VAL.HMIState) | 73
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 74
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(ProdLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 75
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 79
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTE(UDT.FLT.InterruptsDisabled) | 80
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.UsingModuleFault) | 81
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.UsingTableFull) | 82
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 88
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1000,UDT.SET.NextStateNumber) | 91
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1300,UDT.SET.NextStateNumber) | 92
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | RESTARTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(1300,UDT.SET.NextStateNumber) | 93
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | HOLDING LOGIC - Find Restart Position$N$N************************************************************************************************************************************************************************************************************************************************* | OTU(UDT.WRK.Hold) | 95
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | ABORTING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | OTL(UDT.CMD.ClearQueue) | 102
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | SEQUENCING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(2,UDT.SET.NextStateNumber) | 105
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Current User Has Been Released / Aborted Before $NUser Had Become Confirmed User | CLR(UDT.VAL.CurrentUser) | 114
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | MOV(UDT.SEQ.CurrentStep.NextPath,UDT.SET.NextPathNumber) | 145
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.WRK.DevicesVerified) | 146
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | MUL(UDT.SEQ.CurrentStep.FaultTime,1000,UDT.WRK.FaultTimer.PRE) | 147
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | FAULT: Control Module Fault | TON(UDT.WRK.FaultTimer,0,0) | 148
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | Bypass or IDLE State | MOV(UDT.VAL.PathNumber,UDT.WRK.LSStateNumber) | 155
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 158
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[7],UDT.VAL.InUseBy[7],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[7],UDT.VAL.InUseByID[7],UDT.WRK.InUseByAOI[7].UserPriority,UDT.VAL.InUseByTypeArray[7]) | 159
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[15],UDT.VAL.InUseBy[15],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[15],UDT.VAL.InUseByID[15],UDT.WRK.InUseByAOI[15].UserPriority,UDT.VAL.InUseByTypeArray[15]) | 160
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[23],UDT.VAL.InUseBy[23],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[23],UDT.VAL.InUseByID[23],UDT.WRK.InUseByAOI[23].UserPriority,UDT.VAL.InUseByTypeArray[23]) | 161
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[31],UDT.VAL.InUseBy[31],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,UDT.CFG.InUseBitID,UDT.WRK.ModuleStatus,ProdLink,UDT.VAL.InUseByType[31],UDT.VAL.InUseByID[31],UDT.WRK.InUseByAOI[31].UserPriority,UDT.VAL.InUseByTypeArray[31]) | 162
RCOMMENT | EM_RSC_MGR_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(UDT.WRK.Queue[1],UDT.VAL.QueuedUsers[0],UDT.WRK.QueueSizeLessOne) | 164
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_STATUS_V1:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EM_STATUS_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.WRK.UserBit,UDT.CFG.InUseBitID AND 31) | 11
RCOMMENT | EM_STATUS_V1:AOI | Logic | TIMER PRESETS | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 14
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(0,UDT.VAL.HMIState) | 19
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(2,UDT.VAL.HMIState) | 24
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(1,UDT.VAL.HMIState) | 25
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(6,UDT.VAL.HMIState) | 26
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(3,UDT.VAL.HMIState) | 27
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(4,UDT.VAL.HMIState) | 28
RCOMMENT | EM_STATUS_V1:AOI | Logic | Bypass or IDLE State | MOV(5,UDT.VAL.HMIState) | 29
RCOMMENT | EM_STATUS_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyIndex[0],UDT.VAL.UsingID[0],32) | 31
RCOMMENT | EM_STATUS_V1:AOI | Logic | ALARMING LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | NOP() | 63
RCOMMENT | EM_STATUS_V1:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(UDT.FLT.UsingTableFull) | 64
RCOMMENT | EM_STATUS_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InterlockFault) | 65
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPJK_V1:AOI | Logic | Safe State | NOP() | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_V1:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 7
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_V2:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 7
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EM_TEMPVC_VFD_V1:AOI | Logic | ****************$NControls of pump$N************************************** | OTL(Pump.CMD.AutoStop) | 8
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EP_Ctrl_V2:AOI | Logic | Populate Previous User$N | MOV(UDT.WRK.InUseBy1,UDT.WRK.PrevInUseBy1) | 3
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | EX_REQ_V3:AOI | Logic | MAIN LOGIC$N$N************************************************************************************************************************************************************************************************************************************************* | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | EX_REQ_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | MOV(UDT.VAL.TypeArrayRef,InUseByLink.InUseByArray[UDT.CFG.InUseBitID].TypeArrayRef) | 1
RCOMMENT | EX_REQ_V3:AOI | Logic | User ID Word and Bit representation of Integer | MOV(ZoneLink.ZoneID,UDT.VAL.ZoneID) | 2
RCOMMENT | EX_REQ_V3:AOI | Logic | FAULT RESET: Issue a Fault Reset to Any Object Being Used by This EM/EP and Hold For 3 Seconds$N | OTU(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].UsedModuleWarning) | 10
RCOMMENT | EX_REQ_V3:AOI | Logic | POPULATE IN USE BY LISTS$N | COP(InUseByLink.InUseByArray[UDT.CFG.InUseBitID].EMReadyArrayRef[0],UDT.VAL.UsingTypeArray[0],32) | 21
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | LibAnalog_Input:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Alarm_HIHI) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Alarm_HIHI) | 2
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Density_Alarm_HIHI) | 8
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Temp_Alarm_HIHI) | 12
RCOMMENT | libFM:AOI | Logic | **************************************************************************************************** All Level Alarms have a De-Bounce timer to protect from false alarms. If an alarm occurs the alarm will clear via Alarm_Ack but will be reset if the value is still in the alarm condition and will require acknowledgement again. **************************************************************************************************** | OTE(Drive_Gain_Alarm_HIHI) | 16
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** If Auto or Manual and a there is a request to open the valve and interlocks are true then Energize the valve The Interlock must be On for the device to be enabled ************************************************** | TOF(RunDlyOff,?,?) | 6
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** When the Valve is energized and the limit switches are not in the correct position then run the open timer. ************************************************** | TON(RUN_TMR,?,?) | 13
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** When the Valve is de-energized and the limit switches are not in the correct position then run the close timer. ************************************************** | TON(OFF_TMR,?,?) | 15
RCOMMENT | libPump_Mtr:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore only the closed limit is used for fault position If the valve is energized open and the closed limit is still on then the valve is faulted when the timer completes Else if the valve is de-energized and the closed limit is not made then the valve is faulted when the timer completes ************************************************** | OTE(FAULT_STS) | 20
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 1 Calculation$N*************************************************** | CLR(TotalAddedCur[0]) | 32
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 2 Calculation$N*************************************************** | CLR(TotalAddedCur[1]) | 36
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 3 Calculation$N*************************************************** | CLR(TotalAddedCur[2]) | 40
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 4 Calculation$N*************************************************** | CLR(TotalAddedCur[3]) | 44
RCOMMENT | libPump_Mtr:AOI | Logic | ***************************************************$NMeter 5 Calculation$N*************************************************** | CLR(TotalAddedCur[4]) | 48
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** If Auto or Manual and a there is a request to open the valve and interlocks are true then Energize the valve The Interlock must be On for the device to be enabled ************************************************** | TOF(CloseDly,?,?) | 6
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** When the Valve is energized and the limit switches are not in the correct position then run the open timer. ************************************************** | TON(OPEN_TMR,?,?) | 11
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** When the Valve is de-energized and the limit switches are not in the correct position then run the close timer. ************************************************** | TON(CLOSE_TMR,?,?) | 13
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore the Open limit is used to warn the operator of the possible problem If the valve is energized open and the open limit is off then the valve is in warning when the timer completes Else if the valve is de-energized and the Open limit is made then the valve is in warning when the timer completes ************************************************** | OTE(OPEN_FLT) | 16
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ************************************************** This vave type will not fault on the open limit switch therefore only the closed limit is used for fault position If the valve is energized open and the closed limit is still on then the valve is faulted when the timer completes Else if the valve is de-energized and the closed limit is not made then the valve is faulted when the timer completes ************************************************** | OTE(CLOSE_FLT) | 17
RCOMMENT | libValve_ACT_SOL:AOI | Logic | ***************************************************$NMeter Calculation$N*************************************************** | CLR(TotalAddedCur) | 31
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 0
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(UDT.CMD.ResetFault) | 1
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 2
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 3
RCOMMENT | MM_CIR_V1:AOI | EnableInFalse | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 4
RCOMMENT | MM_CIR_V1:AOI | Logic | CM TYPE NUMBER | MOV(FP,UDT.REV.FP) | 0
RCOMMENT | MM_CIR_V1:AOI | Logic | Prevent RECIRC From Causing Module To Go InUse | MOV(0,locIndirectUserID[1]) | 2
RCOMMENT | MM_CIR_V1:AOI | Logic | TIMER PRESETS | DIV(UDT.WRK.tmrTimeInRange.PRE,60000,UDT.CFG.TimeInRange) | 7
RCOMMENT | MM_CIR_V1:AOI | Logic | CONNECTIONS | OTE(UDT.IN.InputHealth) | 8
RCOMMENT | MM_CIR_V1:AOI | Logic | Alarms Enabled | OTU(UDT.STS.AlarmsEnabled) | 9
RCOMMENT | MM_CIR_V1:AOI | Logic | COMMAND: Lock Module | OTU(UDT.STS.Locked) | 10
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | RES(UDT.WRK.InUseResltCntrl) | 17
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | OTE(UDT.STS.InUse) | 18
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | MOV(UDT.VAL.InUseBy[9],UDT.WRK.InUseBy9) | 19
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT RESET: Determine if a Controlling EM/EP is Requesting a Fault Reset$N | OTE(UDT.WRK.ProdZoneFltReset) | 20
RCOMMENT | MM_CIR_V1:AOI | Logic | Reset Faults$N | OTU(UDT.FLT.SystemFaultTimeOFF) | 22
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.STS.WaitInRangeTime) | 23
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Hi) | 24
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTL(UDT.STS.WaitInRangeTime) | 25
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: HHI/LLO Fault Timer | OTE(UDT.FLT.Lo) | 26
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Interlock Faults | OTL(UDT.FLT.InputCard) | 27
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Control Module Fault | OTL(UDT.STS.Faulted) | 33
RCOMMENT | MM_CIR_V1:AOI | Logic | FAULT: Clear Fault Code if No Faults Exist$N | MOV(0,UDT.WRK.FaultCodeHolding) | 34
RCOMMENT | MM_CIR_V1:AOI | Logic | VALUE: PhaseA | CLR(UDT.VAL.PhaseC) | 37
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 1 FAULT UNACKNOWLEDGED | MOV(1,UDT.VAL.HMIState) | 43
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 2$N | MOV(2,UDT.VAL.HMIState) | 44
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 5 NORMAL CONDITIONS | MOV(5,UDT.VAL.HMIState) | 45
RCOMMENT | MM_CIR_V1:AOI | Logic | ****IMPORTANT***$NCHANGES TO THE FOLLOWING RUNGS SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE$N | NOP() | 46
RCOMMENT | MM_CIR_V1:AOI | Logic | CLEAR FAULT CODE$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | CLR(UDT.WRK.ModuleStatus) | 47
RCOMMENT | MM_CIR_V1:AOI | Logic | CLEAR COMMANDS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTU(IN_SuppressAlarms) | 48
RCOMMENT | MM_CIR_V1:AOI | Logic | UDT & CM ENABLE STATUS$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | OTE(STS_Enabled) | 49
RCOMMENT | MM_CIR_V1:AOI | Logic | HMI Device Status: STATE 0: DISABLED$N$N****IMPORTANT***$NCHANGES TO THIS RUNG SHOULD ALSO BE APPLIED TO$NTHE $QEnableInFalse$Q ROUTINE TO ENSURE CONTINUITY WHEN AOI IS DISABLED$NAND WHEN RUNG $QEnableIn$Q IS FALSE | MOV(0,UDT.VAL.HMIState) | 50
RCOMMENT | MM_CIR_V1:AOI | Logic | POPULATE IN USE BY LISTS$N | (UDT.WRK.InUseByAOI[9],UDT.VAL.InUseBy[9],UDT.VAL.Type,UDT.VAL.Index,UDT.VAL.TypeArrayRef,0,UDT.WRK.ModuleStatus,InUseByLink,UDT.VAL.InUseByType[9],UDT.VAL.InUseByID[9],UDT.WRK.InUseByAOI[9].UserPriority,UDT.VAL.InUseByTypeArray[9]) | 51
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_CHAR_V1:AOI | Logic | If raw rate is less than X00, set characterized value to Y00.$NJump to the end of the subroutine.$N | JMP(label_0) | 0
RCOMMENT | SM_CHAR_V1:AOI | Logic | If raw rate is greater than X10, set characterized value to Y10.$NJump to the end of the subroutine. | JMP(label_0) | 1
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X00 and less than X01, move X00 to XL,$NX01 to XG, Y00 to YL and Y01 to YG.$N | MOV(Char.Adjustment_Point[1].Output,CHR_MULT_LOW_VALUE) | 2
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X01 and less than X02, move X01 to XL,$NX02 to XG, Y01 to YL and Y02 to YG.$N | MOV(Char.Adjustment_Point[2].Output,CHR_MULT_LOW_VALUE) | 3
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X02 and less than X03, move X02 to XL,$NX03 to XG, Y02 to YL and Y03 to YG.$N | MOV(Char.Adjustment_Point[3].Output,CHR_MULT_LOW_VALUE) | 4
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X03 and less than X04, move X03 to XL,$NX04 to XG, Y03 to YL and Y04 to YG. | MOV(Char.Adjustment_Point[4].Output,CHR_MULT_LOW_VALUE) | 5
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X04 and less than X05, move X04 to XL,$NX05 to XG, Y04 to YL and Y05 to YG. | MOV(Char.Adjustment_Point[5].Output,CHR_MULT_LOW_VALUE) | 6
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X05 and less than X06, move X05 to XL,$NX06 to XG, Y05 to YL and Y06 to YG. | MOV(Char.Adjustment_Point[6].Output,CHR_MULT_LOW_VALUE) | 7
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X06 and less than X07, move X06 to XL,$NX07 to XG, Y06 to YL and Y07 to YG.$N | MOV(Char.Adjustment_Point[7].Output,CHR_MULT_LOW_VALUE) | 8
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X07 and less than X08, move X07 to XL,$NX08 to XG, Y07 to YL and Y08 to YG. | MOV(Char.Adjustment_Point[8].Output,CHR_MULT_LOW_VALUE) | 9
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X08 and less than X09, move X08 to XL,$NX09 to XG, Y08 to YL and Y09 to YG.$N | MOV(Char.Adjustment_Point[9].Output,CHR_MULT_LOW_VALUE) | 10
RCOMMENT | SM_CHAR_V1:AOI | Logic | If RAW_RATE is greater than or equal to X09 and less than X10, move X09 to XL,$NX10 to XG, Y09 to YL and Y10 to YG. | MOV(Char.Adjustment_Point[10].Output,CHR_MULT_LOW_VALUE) | 11
RCOMMENT | SM_CHAR_V1:AOI | Logic | Calculate the characterized flow rate using the following formula:$NCHAR RATE = (((RAW RATE - XL) / (XG - XL)) * (YG - YL)) + YL | CPT(Char.OUT_Value,(Char.IN_ComparePV-CHR_PROC_LOW_VALUE)/(CHR_PROC_HIGH_VALUE-CHR_PROC_LOW_VALUE)*(CHR_MULT_LOW_VALUE-CHR_MULT_HIGH_VALUE)+CHR_MULT_HIGH_VALUE) | 12
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_Count_V1:AOI | Logic | Copy Unique Valve INDEX to Buffered Location for Code Execution | JMP(label_1) | 0
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | EnableInFalse | No Active Faults Exist | OTU(ExternalFault) | 1
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | No Active Faults Exist | OTU(ExternalFault) | 17
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | Condition Active Fault Latching$N | SUB(FaultBit,1,ActiveFault) | 19
RCOMMENT | SM_ExternalFaultResolve_V1:AOI | Logic | This Is Required For Situations Where Multiple Faults Occur At The Same Time$N | CLR(FaultBit) | 20
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | User ID Word and Bit representation of Integer | CPT(UDT.VAL.UserBit,UserBitID AND 31) | 1
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | Search Through The Source Info Storage Registers for Matching Source$N | OTE(IndexEqual) | 9
RCOMMENT | SM_HoseConnect_V1:AOI | Logic | Search Through The Source Info Storage Registers for Matching Source$N | MOV(UDT.SEQ.Path[locLoopIndex].ID,locSearchValue) | 18
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_IndirectEMAgit_V1:AOI | Logic | Clear Out Old User Info$N | CLR(EM_AGIT.SET.InUseBy[1]) | 1
RCOMMENT | SM_IndirectEMAgit_V1:AOI | Logic | Set user ID Where It Applies$N | MOV(InUseBy1,EM_AGIT.SET.InUseBy[1]) | 2
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_IndirectUsing_V3:AOI | Logic | Unlatch User From Previous Scan If It Is No Longer In Use BUT Also Verify It Hasn$'t Changed Position$N | OTU(AutoEnable[(PrevInUseBy1 AND (NOT 31))/32].[PrevInUseBy1 AND 31]) | 1
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | DISABLE INTERRUPTS FOR FOLLOWING RUNGS$N | UID() | 2
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | REMOVE DATA FROM PREVIOUS USER LIST | OTL(ER) | 3
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | REMOVE DATA FROM PREVIOUS USER LIST | CLR(UserBitID) | 4
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | DETERMINE IF ALREADY IN LIST | OTL(ER) | 7
RCOMMENT | SM_InUseByUsing_V3:AOI | Logic | ENABLE INTERRUPTS | UIE() | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NCapture the current flow rate (in lbs/sec) while the the product is batching (prior to the valve shutoff signal).$N$N**************************************************************************************************************************************$N | DIV(DLY.VAL.Flowrate,60.0,FlowLbPerSecStore) | 0
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf there is an auto addition that just completed shift and update the error samples in the FIFO.$N$N**************************************************************************************************************************************$N | OTL(UpdatePreactCalcs) | 3
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf there are 3 error samples in a row that are all positive or all negative, turn on the command to adjust the preact.$N$N**************************************************************************************************************************************$N | OTE(PreactAdjustCmd) | 5
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf the preact adjust command is on calculate the average error as the total of the last 3 samples divided by 3.$NAlso calculate the error adjustment as:$N$N Preact Error Adjust = Average Error * Preact Adjust Percent / 100.0$N$NIf the flow adjust is not enabled, add the preact error adjust to the current preact setpoint.$N$NIf the flow adjust is enabled, convert the average error from weight in pounds to time in seconds by dividing$Nby the flow rate and add this to the preact time.$N$N**************************************************************************************************************************************$N | ADD(PreactTimeSP,CalcPreactTimeAdj,PreactTimeSP) | 7
RCOMMENT | SM_Preact:AOI | Logic | **************************************************************************************************************************************$N$NIf the preact flow adjust is enabled, calculate the preact as:$N Preact in pounds = Flow Rate in Lb/Sec * Preact Time in seconds$N$N**************************************************************************************************************************************$N | OTL(DLY.CMD.UpdatePreact) | 9
TYPE | SCOPE | ROUTINE | COMMENT | OWNING_ELEMENT | LOCATION
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Initialize All Registers$N | OTU(EnableOut) | 2
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Exit If No Source From MES$N | JMP(Abort) | 3
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value$N | MOV(SourceMES,locSourcePath) | 4
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Search Through The Source Info Storage Registers for Matching SourcePath | MOV(SourceInfo.Table[LoopIndex].Source,SearchValue) | 6
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Abort If Source Not Found In SourceInfo Table$N | JMP(Abort) | 8
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Search Through SourceProp Table To Find Source$N | MOV(SourceProp.Prop[LoopIndex].SourceNo,SearchValue) | 10
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Abort If Source Not Found In SourceProp Table$N | JMP(Abort) | 12
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value After All Tables Have Been Verified$N | MOV(UDT.WRK.CapturedSourcePath,SourcePath) | 13
RCOMMENT | SM_SourceTankValidate_V3:AOI | Logic | Build SourcePath Value After All Tables Have Been Verified$N | MOV(UDT.WRK.CapturedTankPath,TankPath) | 14